## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Sum of EVENT_COUNT | Sum of DISTINCT_UNITS | Sum of MWLost | Sum of MWHrsLost
0010-Thaw shed failure or fire | 1 | 1 | 34.58 | 418.418
0020-Coal car dumpers; shakers; and unloaders | 7 | 7 | 939 | 21914.533
0022-Unloading/receiving hopper (train/truck) | 28 | 28 | 1016 | 8625.0666
0024-Rotary plow | 25 | 25 | 1363 | 48086.9327
0026-Dust suppression system | 2 | 2 | 287.5 | 1941.6667
0028-Dust collection system | 17 | 17 | 2207.5 | 12932.1161
0030-Coal conveyors and feeders | 524 | 524 | 76468.96 | 708096.0852
0035-Metal detector/collector (including magnetic separator) | 1 | 1 | 95 | 163.0833
0040-Coal elevators | 2 | 2 | 120 | 1140
0050-Coal storage fires | 11 | 11 | 4422 | 125012.982
0060-Coal crushers including motors | 31 | 31 | 2047.8 | 50608.7663
0075-Storage silos/hoppers | 44 | 44 | 5414.1 | 19187.5899
0080-Stackers/reclaimers | 34 | 33 | 1103.54 | 11214.073
0084-Coal conveyor scales-storage coal pile | 3 | 3 | 193 | 889.2666
0085-Bunker feeder coal scales | 9 | 9 | 1184.88 | 4438.2264
0090-Bunker fires | 19 | 19 | 1237.75 | 10757.5536
0095-Bunker flow problems | 154 | 153 | 9793.5 | 139998.3442
0100-Bunker gates | 6 | 6 | 471.39 | 1456.9484
0105-Bunker structures | 6 | 6 | 251 | 5364.1332
0106-Coal drying system (see additional codes 0125-0127) | 1 | 1 | 28 | 784
0107-Screen (prior to bunkers) | 7 | 7 | 336 | 2629.5833
0110-Other coal fuel supply problems up through bunkers | 176 | 175 | 22713.51 | 174935.7171
0111-Solid fuel feeder conveyors | 49 | 49 | 1422.12 | 21576.791
0112-Solid fuel feed tanks/hoppers | 1 | 1 | 47.5 | 10.2916
0114-Solid fuel volumetric feeder | 20 | 20 | 182.73 | 1217.93
0115-Solid fuel gravimetric feeder | 6 | 6 | 222.21 | 1157.5848
0116-Solid fuel feeder motors | 5 | 5 | 216.5 | 2331.2249
0119-Solid fuel crushers | 5 | 5 | 88.39 | 549.6317
0121-Other solid fuel feed problems | 210 | 186 | 1590.17 | 13936.3162
0125-Coal crusher dryer hammers | 3 | 3 | 260 | 1692.4166
0126-Coal crusher lube oil system | 3 | 3 | 93.25 | 520.7791
0127-Other coal crusher dryer problems (see code 0106) | 10 | 10 | 1204.16 | 4196.9895
0129-Other coal processing system problems | 47 | 46 | 3959.59 | 34223.0708
0132-Sorbent handling feeders | 2 | 2 | 52.09 | 203.99
0134-Sorbent handling crushers | 2 | 2 | 38.29 | 74.1413
0152-Sorbent feed volumetric feeder | 5 | 5 | 296.8 | 2020.5499
0155-Sorbent feed pneumatic transport system including piping and valves | 2 | 2 | 81 | 480.5
0160-Bed material tanks/hoppers | 1 | 1 | 35.2 | 11196.5333
0163-Bed material feeders | 4 | 4 | 229.16 | 1841.9585
0174-Other bed material handling equipment | 1 | 1 | 37.2 | 1321.84
0200-Pulverizer exhauster fan (for indirect firing) | 31 | 31 | 3455 | 89726.6992
0205-Pulverizer exhauster fan drive | 47 | 47 | 3829.03 | 112389.9339
0210-Pulverizer heater (for indirect firing) | 1 | 1 | 81 | 141.75
0220-Pulverizer system cyclone separator | 1 | 1 | 18 | 107.7
0240-Pulverized coal bin | 61 | 60 | 5556.38 | 22932.5069
0250-Pulverizer feeders | 2472 | 2437 | 190057.49 | 761627.0863
0253-Pulverizer feeder motor | 102 | 102 | 7776.5 | 45229.0067
0255-Pulverizer feeder coal scales | 38 | 38 | 2671.24 | 9977.5843
0256-Seal air system (air to pulverizers) | 21 | 21 | 2281.96 | 11258.1233
0260-Primary air fan | 289 | 288 | 30132.47 | 796334.0526
0262-Primary air fan lube oil system | 16 | 16 | 2924.1 | 14081.7544
0263-Primary air fan drives | 72 | 72 | 10896.54 | 154101.4417
0264-Other primary air fan problems | 112 | 110 | 11274.04 | 164676.8973
0265-Primary air heater | 4 | 4 | 824 | 75630.4996
0266-Primary air heater fouling | 3 | 3 | 100 | 2171.0833
0267-Primary air flow instrumentation | 66 | 66 | 5853.62 | 55512.8851
0270-Primary air duct and dampers | 238 | 238 | 26029.93 | 383614.8336
0280-Pulverizer fires | 134 | 134 | 11858.44 | 258875.352
0290-Pulverizer reduced capacity due to wear | 118 | 118 | 7239.4 | 465983.4977
0300-Pulverizer motors and drives | 217 | 212 | 15833.59 | 331686.5504
0310-Pulverizer mills | 1334 | 1325 | 107981.44 | 1317058.7082
0312-Pulverizer mill classifiers | 56 | 56 | 6564.3 | 45178.2656
0313-Pulverizer mill trunnion seals | 47 | 47 | 4203.16 | 71586.9086
0315-Pulverizer mill coal level controls | 22 | 22 | 1885.03 | 7452.6342
0320-Foreign object in Pulverizers mill | 266 | 263 | 20878.92 | 127299.3014
0325-Pulverizer skidding | 26 | 26 | 1953.33 | 8216.2659
0330-Pulverizer coal leak (pulverizers only) | 161 | 161 | 12008.16 | 151321.6724
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 202 | 202 | 18427.93 | 257380.3017
0335-Pulverizer lube oil system | 176 | 176 | 17285.07 | 98963.1313
0338-Pulverizer control systems (temperature and pressure) | 82 | 82 | 8037.7 | 38738.4008
0339-Pulverizer System Puff | 18 | 18 | 2390.22 | 180435.1587
0340-Other pulverizer problems | 921 | 918 | 78820.75 | 939273.0822
0341-Pulverizer deluge system | 5 | 5 | 619 | 3684.6498
0342-Pulverizer inert system | 11 | 11 | 1169.05 | 16584.1203
0344-Pulverizer inspection | 138 | 138 | 9893.43 | 114105.2438
0345-Pulverizer overhaul | 86 | 86 | 4395.12 | 282135.4707
0346-Pulverizer pyrite removal system | 286 | 286 | 25666.26 | 91727.062
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 263 | 262 | 21517.88 | 250416.5437
0358-Oil burner piping and valves | 19 | 19 | 3112.9 | 14864.2869
0359-Gas burner piping and valves | 81 | 81 | 12916.09 | 55300.3438
0360-Burners | 259 | 255 | 21997.54 | 552465.4102
0361-Burner orfices | 15 | 15 | 999.9 | 25862.7132
0362-Burner tilts | 5 | 5 | 352 | 26242.9331
0366-Duct burners (FBC only) | 9 | 9 | 373.27 | 84107.1766
0370-Burner instruments and controls (except light-off) | 136 | 133 | 16433.71 | 126984.8176
0375-Burner instruments and controls (FBC light-off system) | 1 | 1 | 50 | 564.1667
0380-Light-off (igniter) systems (including fuel supply) | 87 | 87 | 13473.57 | 83508.5425
0385-Igniters | 82 | 82 | 14730.59 | 71207.8092
0390-Burner wind boxes and dampers | 14 | 14 | 1245.1 | 10478.6913
0400-Burner wind box fires | 16 | 16 | 4574.9 | 306307.8643
0410-Other burner problems | 121 | 121 | 7434.25 | 183988.4418
0415-Cyclone feeders | 315 | 314 | 19504.74 | 171556.6372
0420-Cyclone crusher | 18 | 18 | 1194 | 58811.666
0425-Cyclone dampers | 15 | 15 | 1407 | 10371.0159
0426-Cyclone air ducts | 6 | 6 | 622 | 7422.6498
0430-Cyclone furnace | 14 | 14 | 2604.5 | 190702.5329
0435-Other cyclone problems | 355 | 256 | 15741.21 | 117544.1158
0440-Fuel oil pumps (general) | 12 | 12 | 2848.89 | 12002.3534
0441-Fuel oil pumps (burner supply) | 8 | 8 | 1036.56 | 6432.4091
0442-Fuel oil pumps (forwarding/transfer) | 2 | 2 | 638 | 5214.6
0450-Fuel oil heaters | 4 | 4 | 1769.35 | 17218.0727
0460-Fuel oil atomizers | 13 | 13 | 812 | 4544.7165
0470-Oil and gas fires | 2 | 2 | 375.15 | 2831.8124
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 102 | 102 | 14461.66 | 285553.3146
0500-Main steam piping up to turbine stop valves | 201 | 197 | 11632.25 | 268135.9144
0510-Main steam relief/safety valves off superheater | 56 | 56 | 5325.26 | 283266.9106
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 51 | 51 | 14092.84 | 270052.425
0530-Other main steam system problems | 459 | 407 | 8448.77 | 318598.619
0540-Hot reheat steam piping up to turbine stop valves | 31 | 31 | 9127.05 | 1110997.8233
0541-Cold reheat steam piping up to boiler | 19 | 19 | 5866 | 340845.8809
0550-Reheat steam relief/safety valves | 9 | 9 | 418.14 | 7091.9598
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 33 | 33 | 6882.33 | 332565.2036
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 13 | 13 | 3035.8 | 38570.5988
0570-Other reheat steam problems | 183 | 157 | 4839.72 | 1952729.9924
0580-Desuperheater/attemperator piping | 19 | 19 | 2926 | 19428.6153
0590-Desuperheater/attemperator valves | 75 | 74 | 14081.41 | 404659.426
0600-Desuperheater/attemperator spray nozzles | 7 | 7 | 353.25 | 28492.4916
0620-Other desuperheater/attemperator problems | 24 | 24 | 2018.98 | 381257.1629
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 1 | 1 | 383 | 20081.9665
0640-Startup bypass system valves | 32 | 32 | 15253.77 | 420833.7838
0650-Startup bypass tanks or flash tanks | 9 | 9 | 7152.67 | 437470.109
0655-Steam by-pass system instrumentation and controls | 2 | 2 | 1005 | 8223.7496
0660-Other startup bypass system problems | 4 | 4 | 2465 | 143834.033
0670-Feedwater piping downstream of feedwater regulating valve | 12 | 12 | 1885.71 | 48061.2956
0680-Feedwater valves (not feedwater regulating valve) | 46 | 46 | 6492.53 | 492954.869
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 18 | 18 | 4807.45 | 99821.9051
0700-Blowdown system valves A | 8 | 8 | 1881.8 | 65855.1163
0710-Blowdown system piping B | 14 | 14 | 3729.9 | 62038.8239
0720-Blowdown system controls / instrumentation | 4 | 4 | 188 | 618.7332
0730-Other blowdown system problems | 4 | 4 | 823 | 18990.3664
0740-Boiler recirculation pumps | 87 | 87 | 16819 | 820855.8027
0741-Boiler recirculation pumps - motors | 29 | 29 | 6173.39 | 369257.5032
0742-Boiler recirculation pumps - motors - cooling system | 1 | 1 | 55.2 | 75565.12
0750-Boiler recirculation piping including downcomers | 6 | 6 | 1876 | 25026.5662
0760-Boiler recirculation valves | 7 | 7 | 1977.37 | 71498.6898
0770-Other boiler recirculation problems | 14 | 14 | 5068 | 15953.1651
0775-Economizer piping | 33 | 33 | 5527.22 | 289857.0539
0780-Headers between tube bundles | 5 | 5 | 553.33 | 36795.5331
0782-Headers and caps | 3 | 3 | 356 | 82595.4998
0790-Pipe hangers; brackets; supports (general) | 4 | 4 | 1120 | 70888.9828
0799-Other miscellaneous piping system problems | 34 | 34 | 6859.69 | 135283.3813
0800-Drums and drum internals (single drum only) | 65 | 65 | 16917.3 | 134845.6578
0801-HP Drum (including drum level trips not attributable to other causes) | 68 | 68 | 9386.45 | 74813.9369
0802-IP Drum (including drum level trips not attributable to other causes) | 43 | 43 | 8318.78 | 21070.9776
0803-LP Drum (including drum level trips not attributable to other causes) | 25 | 25 | 4145.77 | 15493.7097
0810-Boiler supports and structures (use code 1320 for tube supports) | 2 | 2 | 265 | 156937.5
0814-In-bed bubble caps (FBC only) | 1 | 1 | 32.5 | 3802.5
0820-Casing | 52 | 52 | 8026.08 | 567820.8448
0830-Doors | 31 | 31 | 6577.57 | 62825.86
0840-Refractory and insulation | 42 | 42 | 5098.4 | 320966.9923
0845-Windbox expansion joints | 6 | 6 | 1152 | 341214.8328
0847-Other expansion joints | 5 | 5 | 544 | 39874.3
0848-Inlet panel | 2 | 2 | 10 | 148.4167
0850-Other internal or structural problems | 56 | 56 | 3056.75 | 992571.8202
0855-Drum relief/safety valves (Single drum only) | 28 | 28 | 3074.18 | 59557.6268
0856-HP Drum relief/safety valves | 1 | 1 | 6.5 | 52.5417
0857-IP Drum relief/safety valves | 1 | 1 | 90.7 | 37.7916
0859-Tube external fins/membranes A | 2 | 2 | 538.3 | 19973.6032
0860-Soot blowers - air (see code 3844 for air delivery system) | 19 | 19 | 1906.62 | 30982.5294
0870-Soot blowers - steam | 39 | 39 | 6369.44 | 52857.9977
0872-Soot blowers - water | 5 | 5 | 188 | 1074.1166
0873-Soot blower drives | 4 | 4 | 282 | 2367.1999
0876-Soot blower controls | 22 | 22 | 2732.62 | 23722.6375
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 92 | 92 | 10738.03 | 198692.3702
0885-Fly ash Removal System - wet transport | 8 | 8 | 1489 | 27425.8329
0890-Bottom ash systems (wet or dry) | 178 | 178 | 18428.94 | 508453.8175
0891-Bottom ash hoppers (including gates) | 41 | 41 | 8487.62 | 244776.8476
0892-Bottom ash clinker grinders | 72 | 72 | 11862 | 207469.2963
0893-Bottom ash water pumps and motors | 7 | 7 | 1179.1 | 10086.1511
0894-Bottom ash piping and valves | 28 | 28 | 4859.1 | 50247.4816
0895-Ashpit trouble | 5 | 5 | 315.67 | 14321.4626
0896-Bottom ash dewatering bin system; instruments and controls | 2 | 2 | 568 | 17314.5331
0897-Bottom ash rotary (drag chain type) conveyor and motor | 100 | 100 | 17532.34 | 512636.99
0898-Bottom ash pyrite hopper (pulverizer reject) system | 1 | 1 | 65 | 92.0833
0899-Bottom ash controls and instrumentation | 1 | 1 | 208 | 606.6665
0900-Slag-tap (cyclone furnace) | 22 | 22 | 2005.45 | 64079.4553
0910-Slag-tap (other than cyclone furnace) | 1 | 1 | 180 | 1919.9999
0920-Other slag and ash removal problems A | 413 | 407 | 53317.11 | 1649705.9188
0930-Bed material coolers | 3 | 3 | 25.81 | 1092.79
0931-Bed material transport piping/valves | 13 | 13 | 1524.07 | 65031.1933
0932-Bed material transport tanks/hoppers | 1 | 1 | 37.5 | 27900
0933-Bed material fans/blowers | 6 | 6 | 658.8 | 26739.1896
0936-Bed material conveyors B | 2 | 2 | 61 | 1047.8
0937-Bed material mechanical separators and baghouse | 2 | 2 | 61.28 | 1874.1333
0950-Other bed material system problems | 6 | 6 | 226.6 | 2562.9233
0989-Other bed solids recirculation problems | 26 | 26 | 1603.54 | 57094.7546
0991-Tube leaks | 10 | 10 | 913 | 194896.4165
1000-Waterwall (Furnace wall) | 986 | 985 | 302573.46 | 22726323.7779
1003-Steam generating tubes between steam drum and mud drum | 19 | 19 | 5593.85 | 727231.4906
1005-Generating tubes | 49 | 49 | 5435.21 | 514319.4367
1010-Cyclone furnace (in cyclone area only) | 70 | 70 | 13388.7 | 1086046.3747
1020-Convection pass wall (water tubes only) | 46 | 46 | 13917.84 | 1283200.9826
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 34 | 34 | 11590.88 | 1036089.9044
1035-Platen superheater | 53 | 53 | 23838.1 | 2683117.6933
1040-First superheater | 264 | 264 | 68853.25 | 4682053.2849
1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | 1 | 1 | 118 | 5546
1050-Second superheater | 271 | 271 | 84772.98 | 7717947.3597
1055-External superheater link tubing | 8 | 8 | 2817 | 125296.9652
1060-First reheater | 238 | 238 | 89419.12 | 7430251.4216
1070-Second reheater | 79 | 79 | 28896.49 | 1817213.2473
1075-External reheater link tubing | 2 | 2 | 646 | 47804.8162
1080-Economizer | 213 | 213 | 48973.24 | 4254813.9105
1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | 2 | 2 | 440 | 56453.8331
1090-Other boiler tube leaks | 181 | 177 | 47051.61 | 3569989.4548
1100-Waterwall (Furnace wall) | 153 | 148 | 15794.73 | 462478.0343
1103-Steam generating tubes between steam drum and mud drum | 11 | 11 | 1082.6 | 112273.7415
1105-Generating tubes | 12 | 12 | 297.92 | 28235.9385
1110-Cyclone furnace (in cyclone area only) | 14 | 14 | 853.45 | 16566.4474
1120-Convection pass wall | 15 | 15 | 342 | 17482.4499
1130-Boiler screen; wing wall; or slag screen (water tubes only) | 26 | 26 | 1490.83 | 109112.5425
1140-First superheater | 232 | 221 | 20707.38 | 454923.1245
1150-Second superheater | 106 | 102 | 14283.93 | 285691.0895
1160-First reheater | 94 | 94 | 11449.3 | 584345.6059
1170-Second reheater | 13 | 13 | 603 | 10450.1332
1180-Economizer | 74 | 73 | 3530.88 | 177639.7203
1190-Other tube slagging or fouling | 167 | 167 | 12279.43 | 443544.7372
1191-Bed agglomeration (FBC only) | 9 | 9 | 286.25 | 15147.8771
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 331 | 315 | 26077.83 | 559467.5255
1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | 4 | 4 | 646 | 3288.2164
1300-Water side fouling | 1 | 1 | 40 | 1846
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 6 | 6 | 1097 | 55725.7495
1320-Tube supports/attachments | 1 | 1 | 191 | 5042.4
1330-Slag fall damage | 3 | 3 | 2440 | 856106.3327
1340-Tube modifications (including addition and removal of tubes) | 1 | 1 | 37.5 | 11850
1350-Other miscellaneous boiler tube problems | 256 | 149 | 8998.5 | 499130.7753
1360-Boiler drains system | 7 | 7 | 2187.46 | 33644.9355
1400-Forced draft fans | 184 | 184 | 29057.99 | 1132764.3007
1401-Forced draft fan dampers | 11 | 11 | 2202.12 | 15194.2563
1407-Forced draft fan lubrication system | 27 | 27 | 6862.14 | 66546.2836
1410-Forced draft fan motors | 94 | 94 | 14465.27 | 1227302.7701
1411-Forced draft fan motors - variable speed | 15 | 15 | 2401.95 | 30433.866
1412-Forced draft fan drives (other than motor) | 77 | 77 | 11168.56 | 271956.2099
1413-Forced draft fan couplings | 8 | 8 | 863.86 | 31420.9523
1415-Forced draft fan controls | 126 | 126 | 21538.19 | 279843.176
1420-Other forced draft fan problems | 268 | 264 | 22941.74 | 657440.5587
1421-Secondary air fans/blowers | 13 | 13 | 1387.01 | 11910.5864
1422-Secondary air fan/blower motors - single speed | 2 | 2 | 100.4 | 2364.2666
1423-Secondary air fan/blower motors - variable speed | 1 | 1 | 275 | 247.5
1424-Secondary air fan/blower controls | 11 | 11 | 1565 | 12723.0991
1430-Air supply ducts from FD fan | 51 | 51 | 1462.34 | 341871.9212
1431-Air supply dampers from FD fan | 19 | 19 | 3568 | 64763.7653
1432-Air supply duct expansion joints | 15 | 15 | 4085.1 | 145486.6352
1440-Air supply dampers | 27 | 27 | 2381 | 8430.4663
1450-Other air supply problems | 129 | 125 | 12816.64 | 375482.3174
1455-Induced draft fans | 1120 | 1097 | 79295.54 | 2007921.5624
1456-Induced draft fan dampers | 86 | 86 | 3165.45 | 28262.3825
1457-Induced draft fan lubrication systems | 100 | 100 | 26569.72 | 387821.4577
1460-Induced draft fan fouling | 66 | 66 | 7489 | 129323.6262
1470-Induced draft fan motors and drives | 324 | 321 | 36343.91 | 1286804.9913
1471-Induced draft fan motors - variable speed | 72 | 72 | 10841.72 | 118980.4415
1472-Inducted draft fan coupling | 22 | 22 | 3462.75 | 150841.1198
1475-Induced draft fan controls | 233 | 233 | 39906.48 | 356199.732
1476-Induced draft fan speed changer | 18 | 18 | 3161.17 | 31801.3891
1480-Other induced draft fan problems | 743 | 743 | 52035.33 | 2421266.019
1487-Air heater (tubular) | 25 | 25 | 2583.22 | 154736.4959
1488-Air heater (regenerative) | 243 | 243 | 41371.62 | 2296133.9
1489-Air heater (heat pipe; plate-type) | 9 | 9 | 2679.4 | 69177.6893
1492-Air heater fouling (tubular) | 5 | 5 | 500.1 | 3898.6667
1493-Air heater fouling (regenerative) | 494 | 482 | 12895.46 | 598588.849
1495-Other air heater fouling (heat pipe; plate-type) | 18 | 18 | 3292 | 205243.5654
1500-Air heater soot blowers | 3 | 3 | 104 | 699.8333
1510-Flue gas ducts (except recirculation) | 68 | 67 | 3472.76 | 310159.4243
1512-Flue gas expansion joints | 22 | 22 | 3417.81 | 183387.1206
1520-Flue gas dampers (except recirculation) | 30 | 30 | 5259.25 | 96000.5462
1530-Other flue gas problems | 194 | 194 | 8361.37 | 507724.1035
1535-Flue gas recirculating fan | 11 | 11 | 2400 | 61137.5158
1536-Flue gas recirculating fan dampers | 1 | 1 | 102.5 | 1108.7083
1550-Flue gas recirculation fan motors | 5 | 5 | 379 | 26364.5665
1555-Flue gas recirculation fan controls | 1 | 1 | 317 | 2240.1331
1560-Other flue gas recirculation fan problems | 2 | 2 | 1000 | 3230.4163
1570-Flue gas recirculation ducts | 2 | 2 | 1346 | 262770.7
1580-Flue gas recirculation dampers | 1 | 1 | 2 | 52.8
1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | 2 | 2 | 113 | 109404.9833
1591-Stack damper and linkage | 17 | 15 | 2230.2 | 3732.8857
1592-Stack damper linkage motors | 3 | 3 | 439 | 1022.2664
1599-Other miscellaneous boiler air and gas system problems | 232 | 231 | 15180.24 | 469889.209
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 293 | 293 | 67831.12 | 519287.8094
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 155 | 155 | 21216.47 | 126712.7084
1720-Desuperheater/attemperator controls | 41 | 41 | 7252.23 | 66381.7631
1740-Boiler drum gage glasses/level indicator | 85 | 85 | 21310.81 | 125969.6016
1741-Furnace and water gauge television auxiliary system | 1 | 1 | 153 | 374.85
1750-Burner management system | 177 | 175 | 33419.74 | 211575.7093
1760-Feedwater instrumentation (not local controls) | 35 | 35 | 7127.84 | 46839.5522
1761-Combustion /Steam condition instrumentation (not local controls) | 23 | 23 | 3791.17 | 42799.9126
1762-Desuperheater/attemperator instrumentation (not local controls) | 14 | 14 | 1648.5 | 25616.0494
1799-Other boiler instrumentation and control problems | 251 | 251 | 52114.69 | 435982.8926
1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | 7 | 7 | 607.46 | 205797.7647
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 17 | 17 | 1198.33 | 56950.4404
1810-Other boiler inspections | 13 | 13 | 562.3 | 18074.1864
1811-Boiler Inspections - problem identification/investigative | 7 | 7 | 773.4 | 62738.7954
1812-Boiler Inspections - scheduled or routine | 4 | 4 | 124 | 14212.8
1820-Chemical cleaning/steam blows | 8 | 8 | 1233.1 | 24784.8728
1850-Boiler water condition (not feedwater water quality) | 796 | 796 | 91151.35 | 1085788.2508
1900-Improper balance between tube sections not due to fouling or plugging | 8 | 8 | 953 | 4547.2328
1910-Inadequate air not due to equipment problems | 15 | 15 | 1120.87 | 39624.0348
1980-Boiler safety valve test | 22 | 22 | 2216.1 | 7342.3464
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 36 | 36 | 4975.21 | 46384.1021
1999-Boiler; miscellaneous | 1110 | 1054 | 36369.07 | 3050560.3589
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 15 | 15 | 2291.62 | 28145.2092
2033-Fuel limits - MAPLHGR (Maximum Average Planar Linear Heat Generation Rate - BWR units only) | 1 | 1 | 563 | 1491.95
2035-Core xenon restrictions | 18 | 18 | 5552.69 | 138914.433
2060-Excore nuclear instrumentation | 4 | 4 | 12 | 3553.55
2070-Normal refueling | 3 | 3 | 933.1 | 55111.8197
2071-Refueling equipment problems | 29 | 29 | 1953.09 | 162798.2997
2111-Control rod magnetic jack drives | 4 | 4 | 1919 | 61973.0988
2112-Control rod hydraulic drives | 10 | 10 | 3163.3 | 136496.5701
2120-Control rod scram mechanisms | 1 | 1 | 214 | 1926
2150-Control rod instrumentation | 2 | 2 | 44.7 | 486.3883
2151-Control rod drive controls | 2 | 2 | 736.77 | 38732.0625
2155-Control rod testing | 1 | 1 | 63 | 168
2160-Other control rod drive problems | 4 | 4 | 3826.41 | 290404.3379
2172-Feedwater sparges | 1 | 1 | 459 | 51408
2200-Reactor coolant/recirculating pumps | 11 | 11 | 5636.13 | 1691082.8991
2210-Reactor coolant/recirculating pump motors | 5 | 5 | 3249.89 | 222028.4373
2220-Reactor coolant/recirculating pump MG sets | 12 | 12 | 4147.2 | 126489.8372
2230-Reactor coolant system piping | 6 | 6 | 3703.2 | 243704
2265-Pressurizer (also see codes 2290; 2330; and 2340) | 1 | 1 | 877.7 | 37872.755
2270-Power operated relief and safety/relief valves | 3 | 3 | 1368.96 | 44644.948
2290-Pressurizer spray valves | 3 | 3 | 1650 | 61841.1326
2300-Recirculation loop flow control valves | 1 | 1 | 576 | 40799.9998
2350-BWR feedwater controls | 1 | 1 | 360.23 | 17471.155
2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | 10 | 10 | 4030.67 | 182298.4283
2390-Other reactor coolant system instruments and controls | 3 | 3 | 840.05 | 25850.4025
2399-Other miscellaneous reactor coolant system problems | 1 | 1 | 714 | 3189.1995
2440-Steam generator chemistry (excluding feedwater chemistry) | 1 | 1 | 28.99 | 479.3013
2460-Blowdown system valves B | 7 | 7 | 104.76 | 58421.8523
2470-Blowdown system instruments and controls | 1 | 1 | 20.2 | 302.3267
2480-Other blowdown | 1 | 1 | 23.29 | 92.3837
2510-Main steam isolation valves (BWR and PWR) | 4 | 4 | 3294.96 | 620780.1162
2540-Other steam valves | 5 | 5 | 140.84 | 82049.54
2550-Steam generator instruments (including piping and valves) (no RPS or SAS inputs) | 3 | 3 | 1422 | 73654.7661
2560-Steam generator controls | 1 | 1 | 1047 | 40833
2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | 2 | 2 | 1151 | 147794.2663
2609-Other high pressure injection problems | 1 | 1 | 331.6 | 6046.1732
2625-Accumulators (up to and including check valves) | 1 | 1 | 987 | 155995.35
2628-Residual heat removal/decay heat removal system | 1 | 1 | 1139 | 179962
2630-Safeguard actuation system (including sensors; logic; activators; and sequencers) | 2 | 2 | 1077.7 | 46898.1064
2649-Other emergency core cooling/residual heat removal system problems | 1 | 1 | 37.7 | 192.27
2650-Emergency diesel generators (including actuating systems) | 1 | 1 | 1118 | 100694.5326
2660-Safeguard buses and associated equipment (transformers; breakers; etc.) | 21 | 5 | 2530 | 45008.6995
2680-120V AC safety system power supplies (including inverter) | 2 | 2 | 1626 | 232076.9
2699-Other electrical safety system power supplies (use codes 3600 to 3659 for nonsafety electrical systems) | 1 | 1 | 88.66 | 2152.9603
2720-Containment isolation valves and dampers | 1 | 1 | 91.1 | 440.3166
2805-Moderator systems (CANDU) | 1 | 1 | 30 | 445
2819-Other CVCS and RWC problems | 2 | 2 | 2078 | 69939.0319
2820-Nuclear closed cooling water pumps | 1 | 1 | 21.7 | 15.9133
2821-Nuclear closed cooling water piping | 1 | 1 | 177.2 | 4471.3466
2823-Nuclear closed cooling heat exchanger | 1 | 1 | 581 | 265119.9829
2833-Nuclear service water heat exchangers | 1 | 1 | 166 | 3154
2840-Auxiliary feedwater pumps | 1 | 1 | 1 | 14
2842-Auxiliary feedwater pump steam turbines (including steam control valves) | 1 | 1 | 6.84 | 4.902
2880-Radioactive gas and waste system problems | 3 | 3 | 14.29 | 616.4622
2890-Condenser off-gas system problems | 1 | 1 | 104.68 | 523.4
3110-Condenser tube leaks | 361 | 360 | 74861.55 | 2256534.0163
3111-Condenser tube fouling shell side | 11 | 11 | 1059.15 | 18986.038
3112-Condenser tube fouling tube side | 344 | 339 | 13666.5 | 335952.7234
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 238 | 233 | 24288.62 | 194053.9898
3114-Air-cooled condenser tubes | 9 | 9 | 226.4 | 3389.7782
3115-Air-cooled condenser pumps | 5 | 5 | 965.74 | 9681.4181
3116-Air-cooled condenser fans | 8 | 8 | 653.68 | 926.7212
3118-Other Air-cooled condenser problems | 44 | 40 | 1670.7 | 33274.5327
3119-Other condenser tube casing or shell and internal problems | 1 | 1 | 120 | 318
3120-Tube sheets | 11 | 10 | 779 | 9770.2164
3121-Expansion joint | 9 | 9 | 1901.29 | 112955.1532
3122-Gaskets and seals | 12 | 12 | 1964.12 | 33594.2552
3123-Hot well | 10 | 10 | 1769.2 | 27404.7594
3124-Tube sheet fouling | 56 | 56 | 4433.25 | 65885.3113
3129-Other condenser casing or shell and internal problems | 11 | 11 | 1429.3 | 39561.1829
3130-Air ejectors | 25 | 25 | 3557.16 | 21532.6197
3131-Air ejector piping and valves | 23 | 23 | 2672.85 | 31021.3001
3132-Inter and after condensers | 2 | 2 | 340 | 186
3133-Vacuum pumps | 62 | 62 | 9952.61 | 39668.6626
3134-Vacuum pump piping and valves | 13 | 13 | 2388.5 | 9005.8905
3135-Vacuum pump motor and auxiliaries | 6 | 6 | 1120.25 | 24214.4832
3139-Other air extraction system problems - general | 14 | 14 | 2042.29 | 23308.7801
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 459 | 425 | 43942.54 | 362932.8742
3150-Hot well level controls | 33 | 33 | 6000.31 | 128233.0591
3151-Vacuum pump and air ejector controls | 20 | 13 | 1509.14 | 6019.6028
3159-Other condensing system controls and instruments | 24 | 24 | 6780.5 | 386713.5207
3170-Condenser inspection (use code 3110 to report looking for tube leaks) | 2 | 2 | 634 | 3383.75
3186-Auxiliary Condenser and Associated Equipment | 21 | 21 | 4896.29 | 52166.7634
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 41 | 41 | 5192.37 | 114312.7668
3199-Other miscellaneous condensing system problems | 51 | 51 | 4579.86 | 460745.3542
3210-Circulating water pumps | 242 | 236 | 29073.87 | 1931957.1005
3211-Circulating water pump motors | 174 | 174 | 17759.8 | 884542.2211
3220-Circulating water piping | 35 | 35 | 6238.27 | 252681.7979
3221-Circulating water piping fouling | 35 | 34 | 5649 | 159768.9315
3230-Circulating water valves | 35 | 35 | 8007.9 | 224614.4902
3232-Condenser tube cleaning system including debris filter | 1 | 1 | 150 | 537.5
3233-Circulating water priming system | 3 | 3 | 431 | 841.1997
3235-Cooling tower booster pump | 6 | 6 | 1155.34 | 6231.3631
3238-Cooling tower fan motors | 18 | 18 | 1054.3 | 17206.2248
3239-Cooling tower fan motors - variable speed | 2 | 2 | 41 | 1003.65
3240-Cooling tower fans | 48 | 48 | 1786.5 | 16001.5079
3241-Cooling tower efficiency below design | 23 | 23 | 167.22 | 4826.9859
3242-Cooling tower fill damage | 5 | 5 | 236.92 | 1481.7266
3243-Cooling tower icing | 32 | 32 | 4290 | 140104.1992
3245-Other cooling tower problems | 48 | 48 | 6578.38 | 1147880.9244
3246-Cooling tower fouling | 6 | 6 | 79 | 2952.9166
3247-Cooling tower instrumentation | 18 | 18 | 3103.7 | 13031.5137
3250-Circulating water system instruments and controls | 13 | 13 | 3484.9 | 53219.5223
3260-Traveling screens | 57 | 57 | 6537.04 | 122498.4552
3261-Traveling screen fouling | 116 | 107 | 17470.2 | 71437.943
3269-Circulating water biological conditions (ie; zebra mussels) | 1 | 1 | 265 | 1060
3270-Intake system problems other than traveling screens | 58 | 58 | 6561 | 188487.7642
3271-Intake grating fouling | 24 | 24 | 3692.1 | 44169.8509
3272-Circulating water screenwash system | 4 | 4 | 1489 | 13031.6495
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 63 | 63 | 10639.45 | 486262.4428
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 22 | 22 | 4344.8 | 78282.8853
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 100 | 98 | 2394.03 | 98712.7291
3285-Circulating water chemistry | 19 | 17 | 2276.5 | 29855.9328
3290-Waste water (zero discharge) tanks; pumps and motors | 3 | 3 | 367.53 | 63142.3918
3291-Waste water (zero discharge) system fouling | 2 | 2 | 457 | 3643.7
3299-Other circulating water system problems | 66 | 64 | 7313.57 | 1039575.3202
3300-Condensate water pre-treatment | 17 | 17 | 2763 | 172070.016
3310-Condensate/hotwell pumps | 112 | 112 | 16213.45 | 843165.9878
3311-Condensate/hotwell pump motor | 48 | 48 | 5992.05 | 285605.7971
3312-Condensate booster pump | 23 | 23 | 4879.7 | 138751.8131
3313-Condensate booster pump motor | 5 | 5 | 1736 | 40621.8999
3314-Condensate booster pump motor - variable speed | 9 | 9 | 1453.78 | 24198.3699
3320-Condensate piping | 29 | 29 | 5533.68 | 65516.2909
3330-Condensate valves | 45 | 44 | 10167.05 | 124787.0406
3340-LP heater tube leaks | 22 | 22 | 3950.77 | 168720.0094
3341-Other LP heater - general | 44 | 44 | 7926.72 | 297084.1225
3342-IP heater tube leaks | 19 | 19 | 961 | 91399.983
3343-Other IP heater - general | 16 | 16 | 1455.97 | 25886.6079
3344-Deaerator (including level control) | 102 | 102 | 20481.27 | 370930.8469
3350-Condensate polishing and filtering systems | 64 | 64 | 9066.81 | 226820.5702
3351-Chemical addition systems | 7 | 7 | 2316 | 59092.1496
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 146 | 146 | 20993.45 | 408063.2638
3360-Condensate makeup and return (including storage tanks) | 35 | 35 | 5686.8 | 83789.843
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 24 | 24 | 4170.4 | 33825.9421
3380-Condensate coolers | 8 | 8 | 272 | 30827.3999
3399-Other miscellaneous condensate system problems | 47 | 47 | 7817.11 | 74505.1728
3401-Startup feedwater pump | 32 | 32 | 8949 | 171857.914
3402-Startup feedwater pump drives - all types | 5 | 5 | 1953 | 18389.0495
3407-Feedwater pump suction screens | 16 | 16 | 3433.5 | 165420.2075
3408-Feedwater pump drive - local controls | 88 | 88 | 26564.4 | 304273.5813
3409-Feedwater pump drive motor - variable speed | 9 | 9 | 1381 | 25467.5164
3410-Feedwater pump | 528 | 525 | 97821.03 | 2959628.0377
3411-Feedwater pump drive - motor | 120 | 120 | 13147.68 | 1384960.4755
3412-Feedwater pump drive - steam turbine | 167 | 167 | 44551.44 | 693183.8403
3413-Feedwater pump coupling and drive shaft | 43 | 43 | 6676.39 | 421381.0795
3414-Feedwater pump local controls | 106 | 106 | 29593.11 | 431839.1295
3415-Feedwater pump/drive lube oil system | 159 | 159 | 34411.85 | 499785.5214
3416-Other feedwater pump problems | 198 | 174 | 33705.41 | 1101742.4164
3417-Feedwater pump drive - main shaft | 14 | 14 | 2773.92 | 126284.3757
3418-Feedwater pump drive - other | 28 | 28 | 6494.5 | 82094.3041
3419-Feedwater pump drive - gear | 2 | 2 | 441 | 42852.5832
3420-Feedwater piping and supports | 58 | 58 | 11811.77 | 409174.1182
3430-Feedwater regulating (boiler level control) valve | 147 | 147 | 27192.96 | 405281.9845
3431-Other feedwater valves | 203 | 203 | 48305.4 | 1467149.6074
3439-HP heater head leaks | 40 | 40 | 2471.78 | 110199.0764
3440-High pressure heater tube leaks | 282 | 282 | 20332.59 | 1647433.7286
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 95 | 95 | 7197.6 | 234988.3379
3453-Feedwater Booster Pump Drive Motor - Variable Speed | 1 | 1 | 44 | 29.3333
3454-Feedwater Booster Pump | 22 | 22 | 6552.3 | 207279.116
3455-Feedwater Booster Pump Drive - Motor | 3 | 3 | 765 | 12392.8164
3456-Feedwater Booster Pump Drive - Steam Turbine | 2 | 2 | 201 | 292.95
3457-Feedwater Booster Pump Coupling and Drive Shaft | 3 | 3 | 661.8 | 42832.51
3458-Feedwater Booster Pump Local Controls | 2 | 2 | 768 | 28202.9997
3459-Feedwater Booster Pump/Drive Lube Oil System | 4 | 4 | 660.6 | 5190.883
3460-Other Feedwater Booster Pump Problems | 11 | 11 | 2613 | 278555.366
3499-Other feedwater system problems | 215 | 214 | 28390.93 | 546617.2671
3501-Heater drain pumps | 33 | 33 | 3220.2 | 606062.2906
3502-Heater level control | 50 | 49 | 5587.75 | 50170.3034
3503-Heater drain piping | 19 | 19 | 1646.7 | 133128.8482
3504-Heater drain valves | 53 | 52 | 4625.34 | 427924.0432
3505-Heater drain pump drive | 3 | 3 | 240 | 7264.9999
3509-Other heater drain system problems | 11 | 11 | 692 | 10775.483
3520-HP Extraction steam piping | 14 | 14 | 2050.43 | 90873.678
3521-HP Extraction steam valves | 17 | 16 | 2739.62 | 272269.0437
3522-HP Extraction steam instruments and controls | 3 | 3 | 266.54 | 250.7276
3529-Other HP extraction steam system problems | 7 | 7 | 1163 | 147959.1999
3530-IP Extraction steam piping | 10 | 10 | 2340 | 75552.4827
3531-IP Extraction steam valves | 6 | 6 | 762.66 | 31097.4984
3532-IP Extraction steam instruments and controls | 1 | 1 | 25 | 16.25
3539-Other IP extraction steam system problems | 1 | 1 | 3 | 33
3540-LP Extraction steam piping | 9 | 9 | 1747 | 258405.1328
3541-LP Extraction steam valves | 6 | 6 | 771.17 | 12413.3386
3542-LP Extraction steam instruments and controls | 1 | 1 | 44 | 166.4667
3549-Other LP extraction steam system problems | 4 | 4 | 604.58 | 18807.4665
3600-Switchyard transformers and associated cooling systems - external | 47 | 47 | 3920.91 | 365787.4635
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 8 | 8 | 1231.69 | 104512.3974
3610-Switchyard circuit breakers - (not outside management control) | 62 | 62 | 12115 | 207016.2399
3611-Switchyard circuit breakers - external | 122 | 121 | 18424.55 | 458882.9257
3612-Switchyard system protection devices - external | 148 | 148 | 22426.34 | 782689.5387
3613-Switchyard system protection devices - (not outside management control) | 31 | 31 | 3901.51 | 22252.1621
3618-Other switchyard equipment ? (not outside management control) | 25 | 25 | 4124.06 | 112155.6615
3619-Other switchyard equipment - external | 252 | 222 | 14296.85 | 1136906.1117
3620-Main transformer | 517 | 517 | 64592.25 | 10202110.8274
3621-Unit auxiliaries transformer | 120 | 118 | 22747.9 | 1742233.5176
3622-Station service startup transformer | 37 | 37 | 5254.45 | 82328.9404
3623-Auxiliary generators | 3 | 3 | 184 | 142.85
3624-Generator Voltage Supply System | 30 | 30 | 2906.98 | 451706.1714
3629-Other switchyard or high voltage system problems - external | 213 | 209 | 16855.69 | 3079547.1659
3630-480-volt transformers | 17 | 17 | 3893.68 | 128944.4845
3631-480-volt circuit breakers | 143 | 141 | 25681.07 | 181066.7908
3632-480-volt conductors and buses | 44 | 44 | 8028.85 | 183232.7427
3634-480-volt protection devices | 22 | 22 | 5813.22 | 48249.2828
3639-Other 480-volt problems | 23 | 23 | 3143.52 | 23094.8041
3640-AC instrument power transformers | 4 | 4 | 920.5 | 14011.2994
3641-AC Circuit breakers | 88 | 88 | 11992.45 | 186916.7291
3642-AC Conductors and buses | 48 | 48 | 8522 | 4403888.5038
3643-AC Inverters | 29 | 29 | 4446.15 | 67332.8307
3644-AC Protection devices | 157 | 157 | 20180.35 | 2350333.0541
3649-Other AC instrument power problems | 31 | 31 | 3520.61 | 123633.4207
3650-DC instrument power battery chargers | 16 | 16 | 1709.72 | 34271.5049
3651-DC circuit breakers | 11 | 11 | 999.9 | 24361.3964
3652-DC conductors and buses | 12 | 12 | 1709.08 | 14204.5468
3653-DC protection devices | 30 | 30 | 3613.69 | 56161.9357
3659-Other DC power problems | 60 | 60 | 6707.08 | 231802.8994
3660-4160-volt transformers | 19 | 19 | 5666 | 774029.8977
3661-4160-volt circuit breakers | 113 | 113 | 23070.9 | 370016.2573
3662-4160-volt conductors and buses | 49 | 48 | 15654 | 485990.6791
3663-4160-volt insulators | 1 | 1 | 347 | 121.45
3664-4160-volt protection devices | 38 | 38 | 6823.82 | 150389.4551
3669-Other 4160-volt problems | 32 | 32 | 6176.5 | 190637.3366
3670-12kV transformers | 22 | 22 | 4884.41 | 142670.2099
3671-12kV circuit breakers | 60 | 60 | 6139.65 | 211638.6456
3672-12kV conductors and buses | 45 | 45 | 3834.05 | 1831256.1327
3673-12kV insulators | 4 | 4 | 155.65 | 8113.5725
3674-12kV protection devices | 25 | 25 | 2523.5 | 112749.1401
3679-Other 12kV problems | 15 | 15 | 782.8 | 20239.5365
3680-Other voltage system transformers | 11 | 11 | 2022.88 | 21331.4376
3681-Other voltage system breakers | 65 | 65 | 7048.6 | 178929.8457
3682-Other voltage system conductors and buses | 13 | 13 | 2887 | 1484173.766
3683-Other voltage system insulators | 9 | 9 | 1324.13 | 371050.9127
3684-Other voltage system protection devices | 41 | 41 | 5439.89 | 576627.1596
3689-Other Other voltage system problems | 51 | 51 | 8098.78 | 152064.8498
3690-Station Service Power Distribution System; General | 78 | 78 | 12959.31 | 474116.9388
3700-Power Station switchyard (non generating unit equipment) | 32 | 32 | 2761.17 | 42482.2672
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 89 | 89 | 6353 | 140190.331
3720-Transmission equipment at the 1st substation) | 29 | 28 | 4728.59 | 106370.5655
3730-Transmission equipment beyond the 1st substation | 103 | 102 | 8553.59 | 281851.9047
3800-Open cooling water pumps and motors | 5 | 5 | 870 | 2030.6329
3805-Open cooling water system instrumentation | 3 | 3 | 1706 | 18984.45
3810-Service water pumps and motors | 19 | 19 | 1824.1 | 50722.0496
3811-Service water piping | 36 | 35 | 3046.06 | 72209.728
3812-Service water valves | 5 | 5 | 859.94 | 14032.3733
3813-Service water heat exchangers | 6 | 6 | 454 | 65422.6832
3814-Service water system fouling | 19 | 19 | 2859.01 | 32996.9883
3815-Service water strainer | 1 | 1 | 180 | 464.9999
3819-Other service water problems A | 21 | 21 | 1825.2 | 17802.7543
3820-Closed cooling water pumps | 34 | 34 | 3837.08 | 93405.8285
3821-Closed cooling water piping | 16 | 16 | 1634.07 | 32156.3169
3822-Closed cooling water valves | 12 | 12 | 1776.25 | 16160.7751
3823-Closed cooling water heat exchangers | 12 | 12 | 1608.98 | 25992.9636
3824-Closed cooling water system fouling | 6 | 6 | 358.79 | 9142.6472
3825-Closed cooling water instrumentation | 6 | 6 | 1104 | 2759.6331
3826-Closed cooling water strainer | 2 | 2 | 786 | 66015.7497
3829-Other closed cooling water system problems A | 50 | 50 | 5644.5 | 78955.0656
3830-Auxiliary boiler | 29 | 29 | 11208.15 | 385079.0024
3831-Auxiliary steam piping | 11 | 11 | 932.22 | 16418.1338
3832-Auxiliary steam valves | 27 | 27 | 6174.1 | 93428.7949
3833-Auxiliary steam controls and instruments | 10 | 10 | 2810.76 | 42509.3325
3834-Auxiliary boiler tube leaks | 1 | 1 | 736 | 14720
3835-Auxiliary boiler burner management system | 2 | 2 | 574 | 3061.6331
3836-Steam Transfer to Other Unit | 174 | 173 | 14992.14 | 375930.1123
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 28 | 28 | 3061.16 | 36165.9692
3840-Service air compressors | 35 | 35 | 4776.86 | 36906.3413
3841-Service air piping | 12 | 12 | 2135.9 | 92503.8627
3843-Service air dryers | 3 | 3 | 189.1 | 349.4
3844-Soot blowing air compressor and system | 26 | 26 | 2579.09 | 53671.1289
3849-Other service air problems | 4 | 4 | 142.3 | 883.5199
3850-Instrument air compressors | 33 | 33 | 5331.6 | 93861.3039
3851-Instrument air piping | 11 | 11 | 1169.66 | 11085.2132
3852-Instrument air valves | 10 | 10 | 2639.94 | 11145.5738
3853-Instrument air dryers | 19 | 19 | 4242 | 25319.9815
3859-Other instrument air problems | 21 | 21 | 4470.39 | 75351.5729
3860-Fire protection system pumps | 1 | 1 | 175 | 13498.3333
3861-Fire protection system piping | 5 | 5 | 538 | 145398.9249
3862-Fire protection system valves | 11 | 11 | 2305.23 | 36862.5917
3863-Fire protection system fouling | 1 | 1 | 48 | 284
3864-Fire protection system instrumentation and controls | 98 | 98 | 9192.68 | 108927.5399
3869-Other fire protection system problems | 61 | 61 | 5996.61 | 167664.8939
3870-Fuel Gas Compressor and Motors | 53 | 53 | 2071.92 | 31720.2943
3871-Fuel Gas Compressor Piping | 5 | 5 | 199 | 4930.7999
3872-Fuel Gas Compressor Valves | 41 | 41 | 4327.56 | 23636.6173
3873-Fuel Gas Compressor Heat Exchangers | 8 | 8 | 435.76 | 4608.3885
3874-Fuel Gas Compressor Controls and Instrumentation | 70 | 69 | 4113.23 | 22607.5479
3875-Fuel Gas Compressor Filters | 6 | 6 | 265.94 | 327.5389
3876-Fuel Gas Compressor Fire System | 10 | 10 | 1146.88 | 2356.8089
3879-Fuel Gas Compressor - other | 71 | 70 | 4668.01 | 47893.7146
3880-Seal air fan | 1 | 1 | 435 | 761.25
3882-Seal air control dampers and drives | 2 | 2 | 172 | 227.05
3889-Other seal air fan system problems | 1 | 1 | 167 | 208.75
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 93 | 93 | 9467.79 | 78093.2674
3899-Other miscellaneous auxiliary system problems | 130 | 130 | 13227.22 | 109181.0634
3950-Process computer | 53 | 53 | 4697.47 | 67392.401
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 296 | 277 | 4544.19 | 1821152.7367
3970-Distributive Control System (DCS) - process computer | 62 | 62 | 10054.95 | 326532.8702
3971-DCS - data highway | 59 | 59 | 8344.02 | 111890.9372
3972-DCS - hardware problems (including card failure) | 119 | 119 | 19426.82 | 243007.7231
3973-DCS - internal and termination wiring | 21 | 19 | 1719.05 | 4943.0704
3974-DCS - logic problems | 124 | 121 | 13558.84 | 109054.644
3975-DCS - upgrades | 31 | 31 | 5306.32 | 81098.4208
3979-Other DCS problems | 69 | 69 | 10218.13 | 267759.7813
3980-Programmable Logic Controller (PLC) | 26 | 26 | 1758.41 | 8066.9351
3981-PLC - data highway | 20 | 20 | 1635.15 | 38833.6159
3982-PLC - hardware problems (including card failure) | 36 | 36 | 3610.51 | 29212.5708
3983-PLC - internal and termination wiring | 5 | 5 | 354 | 1485.9165
3984-PLC - logic problems | 17 | 17 | 1843.08 | 15239.5984
3985-PLC - upgrades | 1 | 1 | 38 | 50.6667
3989-Other PLC problems | 6 | 6 | 352.5 | 1216.0249
3995-Powerhouse heating and ventilating systems | 9 | 9 | 1564.5 | 13196.2742
3996-Air conditioning systems - rooms and areas | 10 | 10 | 1337 | 15058.0927
3998-Balance of plant overhaul/outage | 6 | 6 | 173 | 7401.2667
3999-Other miscellaneous balance of plant problems | 476 | 475 | 47172.21 | 2222989.4427
4000-Outer casing A | 12 | 12 | 3065.54 | 252028.272
4001-Inner casing C | 4 | 4 | 1204 | 3398.8665
4010-Nozzles and nozzle blocks C | 9 | 9 | 368.7 | 155876.2232
4011-Diaphragms A | 4 | 4 | 604 | 670445.5
4012-Buckets or blades A | 2 | 2 | 516 | 4665.4999
4014-Bucket or blade fouling C | 345 | 255 | 2994.13 | 521614.7478
4020-Shaft seals B | 118 | 88 | 1805.82 | 319952.6611
4022-Gland rings C | 4 | 4 | 2000 | 58766.6655
4030-Rotor shaft C | 21 | 21 | 6942.55 | 2882451.7727
4040-Bearings C | 172 | 171 | 33191.72 | 2732702.5641
4041-HP steam turbine thrust bearings | 13 | 13 | 4154.7 | 506941.1645
4099-Other high pressure turbine problems | 2053 | 1749 | 60283.53 | 1804093.4969
4100-Outer casing B | 1 | 1 | 250 | 162.5
4101-Inner casing B | 2 | 2 | 328 | 184.8664
4112-Buckets or blades B | 1 | 1 | 155 | 159825.6666
4113-Bucket or blade fouling B | 2 | 1 | 9 | 215.85
4120-Shaft seals C | 1 | 1 | 5 | 37.5
4122-Gland rings B | 1 | 1 | 67 | 1442.7333
4130-Rotor shaft B | 1 | 1 | 163 | 652
4140-Bearings D | 33 | 30 | 7381.58 | 347464.7106
4199-Other intermediate pressure turbine problems | 34 | 34 | 12681.8 | 519359.2589
4200-Outer casing C | 2 | 2 | 255 | 562.4166
4201-Inner casing A | 2 | 2 | 765 | 12473.9998
4211-Diaphragms C | 7 | 7 | 1291 | 9383.1661
4212-Buckets or blades C | 48 | 48 | 4614.4 | 3620116.1421
4213-Bucket or blade fouling A | 1 | 1 | 35 | 77315
4220-Shaft seals D | 11 | 11 | 3415.9 | 229194.9465
4240-Bearings E | 37 | 35 | 6177.8 | 294526.2851
4241-LP steam turbine thrust bearings | 3 | 3 | 257 | 845.65
4250-Other low pressure turbine problems | 113 | 113 | 23827.84 | 4800733.821
4260-Main stop valves | 167 | 167 | 30626.66 | 1325790.1398
4261-Control valves | 366 | 360 | 60680.71 | 1689176.358
4262-Intercept valves | 66 | 66 | 18023.21 | 248743.6849
4263-Reheat stop valves | 39 | 39 | 8315.99 | 119082.2617
4264-Combined intercept valves | 18 | 18 | 5928.8 | 77868.0151
4265-Miscellaneous drain and vent valves | 24 | 24 | 4797.61 | 99835.9759
4266-Main stop valve testing | 55 | 52 | 9889.62 | 51271.4869
4267-Control valve testing | 86 | 86 | 13652.43 | 136384.0577
4268-Reheat/intercept valve testing | 21 | 21 | 5368.5 | 84080.7565
4269-Other turbine valves (including LP steam admission valves) | 91 | 91 | 16421.49 | 282834.1217
4270-Crossover or under piping | 22 | 22 | 7026.1 | 401739.2034
4279-Miscellaneous turbine piping | 49 | 49 | 12878.5 | 939376.5458
4280-Lube oil pumps A | 43 | 43 | 10352.1 | 381880.5849
4281-Lube oil coolers A | 40 | 40 | 7714.4 | 440643.4834
4282-Lube oil conditioners | 1 | 1 | 26 | 710.6667
4283-Lube oil system valves and piping | 14 | 14 | 3271.06 | 52190.9417
4284-Lube oil pump drive | 12 | 12 | 2338.8 | 127425.5097
4289-Other lube oil system problems | 58 | 58 | 9209.63 | 207726.7563
4290-Hydraulic system pumps | 20 | 20 | 3828 | 91164.7153
4292-Hydraulic system filters | 11 | 11 | 1822 | 26855.7824
4293-Hydraulic system pipes and valves | 115 | 115 | 32175.54 | 494918.4529
4299-Other hydraulic system problems | 71 | 71 | 15215.51 | 503639.9495
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 82 | 82 | 15763.87 | 148446.0112
4301-Turbine governing system | 134 | 133 | 16127.73 | 356963.8999
4302-Turbine trip devices (including instruments) | 238 | 235 | 54738.29 | 593638.7812
4303-Exhaust hood and spray controls | 12 | 12 | 3000.02 | 22302.9101
4304-Automatic turbine control systems - mechanical | 8 | 8 | 1216 | 18732.3163
4305-Automatic turbine control systems - mechanical - hydraulic | 19 | 19 | 3603.94 | 57130.0873
4306-Automatic turbine control systems - electro-hydraulic - analog | 8 | 8 | 2511.35 | 52341.6055
4307-Automatic turbine control systems - electro-hydraulic - digital | 23 | 23 | 3745.39 | 29947.1875
4308-Automatic turbine control systems - digital control and monitoring | 58 | 57 | 12724.97 | 344880.541
4309-Other turbine instrument and control problems | 136 | 136 | 27524.29 | 363781.1169
4310-Steam Turbine Control System - data highway | 9 | 9 | 2459 | 66180.5822
4311-Steam Turbine Control System - hardware problems (including card failure) | 60 | 60 | 12966.99 | 209028.8511
4312-Steam Turbine Control System - internal and termination wiring | 5 | 5 | 929.06 | 3954.4478
4313-Steam Turbine Control System - logic problems | 50 | 50 | 11516.64 | 125022.1856
4314-Steam Turbine Control System - upgrades | 4 | 4 | 300.72 | 962.9106
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 19 | 18 | 3029.04 | 2040557.3736
4401-Inspection F | 3 | 3 | 522 | 121848.0999
4402-Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 7 | 7 | 1286.66 | 32746.3568
4410-Turning gear and motor A | 42 | 42 | 7086.66 | 240074.7307
4411-Steam turbine gear box (single shaft configuration) | 2 | 2 | 310 | 9592.1665
4415-Shaft coupling mechanism | 1 | 1 | 92 | 2554.5333
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 222 | 218 | 51125.35 | 2060571.4235
4430-Gland seal system | 63 | 63 | 13635.19 | 367133.505
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 15 | 15 | 1305.36 | 116921.37
4445-Steam reheater | 7 | 7 | 1551.52 | 4396.5905
4450-Water induction | 21 | 21 | 3800.4 | 125552.2635
4460-Turbine overspeed trip test | 16 | 16 | 5410.3 | 47178.1085
4470-Differential expansion | 66 | 65 | 19832.99 | 122935.2616
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 28 | 28 | 1894.36 | 21346.3293
4499-Other miscellaneous steam turbine problems | 344 | 338 | 41939.45 | 1893900.1586
4500-Rotor windings (including damper windings and fan blades on hydro units) | 37 | 37 | 4361.41 | 3002272.1866
4510-Rotor collector rings | 14 | 14 | 2348.89 | 226700.1831
4511-Rotor; General | 41 | 41 | 4298.33 | 1808269.3071
4520-Stator windings; bushings; and terminals | 50 | 50 | 7033.84 | 3427424.435
4530-Stator core iron | 1 | 1 | 785 | 768344.9164
4535-Stator; General | 50 | 50 | 8197.4 | 2428680.9663
4540-Brushes and brush rigging | 33 | 33 | 5599.49 | 530298.1984
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 130 | 128 | 15559.07 | 1367938.6779
4551-Generator bearings | 92 | 92 | 17798.84 | 1420499.8224
4552-Generator lube oil system | 131 | 114 | 7789.05 | 191749.9405
4555-Bearing cooling system A | 63 | 63 | 4690.41 | 70215.2579
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 110 | 109 | 13975.79 | 2581339.4561
4570-Generator casing | 9 | 9 | 1651.01 | 146839.081
4580-Generator end bells and bolting | 2 | 2 | 712 | 52240.6665
4590-Generator brakes | 69 | 67 | 4857.15 | 193360.7631
4600-Exciter drive - motor | 17 | 17 | 2796.34 | 75424.1147
4601-Exciter field rheostat | 25 | 25 | 3079.15 | 27947.8887
4602-Exciter commutator and brushes | 43 | 43 | 11189.83 | 1034173.2009
4603-Solid state exciter element | 76 | 76 | 16354.47 | 666960.6575
4604-Exciter drive - shaft | 7 | 7 | 2498 | 11484.3658
4605-Exciter transformer | 111 | 110 | 2342.55 | 105841.8469
4609-Other exciter problems | 597 | 595 | 96813.91 | 4035947.7085
4610-Hydrogen cooling system piping and valves | 28 | 28 | 5256.69 | 341013.2276
4611-Hydrogen coolers | 54 | 54 | 5306.5 | 672746.0146
4612-Hydrogen storage system | 3 | 3 | 508.5 | 170405.7499
4613-Hydrogen seals | 17 | 17 | 3658.43 | 277993.5889
4619-Other hydrogen system problems | 46 | 46 | 11289.94 | 1587321.1589
4620-Air cooling system | 68 | 68 | 6685.62 | 103848.5069
4630-Liquid cooling system | 60 | 60 | 18778.32 | 408519.4206
4640-Seal oil system and seals A | 48 | 48 | 14561.11 | 881781.8731
4650-Other cooling system problems | 71 | 71 | 7656.68 | 150461.0067
4700-Generator voltage control | 282 | 276 | 40412.65 | 1418168.7865
4710-Generator metering devices | 74 | 74 | 12743.58 | 340177.0497
4720-Generator synchronization equipment | 221 | 216 | 20965.17 | 357992.6219
4730-Generator current and potential transformers | 132 | 132 | 24243 | 827779.3763
4740-Emergency generator trip devices | 227 | 227 | 35208.94 | 5052384.8061
4750-Other generator controls and metering problems | 339 | 338 | 36779.48 | 607502.2591
4800-Generator main leads | 28 | 28 | 4517.55 | 289139.2154
4805-Generator Bus Duct Cooling System | 30 | 30 | 6249.94 | 939157.1306
4810-Generator output breaker | 389 | 383 | 38593.07 | 2061527.4418
4830-Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 21 | 21 | 3333.4 | 135994.299
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 4 | 4 | 1132.16 | 12289.0033
4840-Inspection E | 7 | 7 | 1819.1 | 5276.4413
4842-Reactive and capability testing | 8 | 8 | 1419.43 | 87122.5926
4850-Core monitor alarm | 4 | 4 | 445.8 | 36459.1032
4860-Generator Neutral Grounding Equipment | 28 | 28 | 9496.07 | 429162.4865
4899-Other miscellaneous generator problems | 482 | 482 | 49398.82 | 3282228.3506
5000-Inlet air ducts A | 22 | 22 | 2395.45 | 175159.1309
5001-Inlet air vanes / nozzles | 167 | 166 | 21334.87 | 236555.0733
5002-Inlet air filters A | 303 | 303 | 23205.18 | 219372.2754
5003-Inlet cone | 2 | 2 | 360 | 77041.8999
5004-Inlet air chillers B | 37 | 37 | 573.74 | 120605.7477
5005-Inlet air evaporative coolers B | 56 | 56 | 669.86 | 8691.1394
5006-Inlet air foggers B | 16 | 16 | 592.64 | 104512.0075
5009-Other inlet air problems A | 73 | 72 | 8348.16 | 158731.2192
5010-High pressure shaft D | 1 | 1 | 90 | 15615
5011-High pressure bearings C | 4 | 4 | 444 | 25502.1666
5012-High pressure blades/buckets B | 7 | 7 | 734.46 | 173965.077
5013-Compressor casing and bolts | 10 | 10 | 1469.69 | 291180.6258
5014-Compressor diaphragms | 8 | 8 | 778.8 | 21195.3096
5015-Compressor seals | 3 | 3 | 199.5 | 3476.3166
5016-High pressure compressor bleed valves | 157 | 154 | 19068.21 | 91075.0266
5017-Low pressure compressor bleed valves | 47 | 47 | 6010.2 | 24310.2593
5019-Other high pressure problems A | 17 | 17 | 2438.59 | 288225.4269
5020-Low pressure shaft D | 1 | 1 | 98.1 | 668.7149
5021-Low pressure bearings D | 3 | 3 | 546 | 5461.6166
5022-Low pressure blades/buckets A | 54 | 51 | 559.5 | 292675.4082
5029-Other low pressure problems E | 10 | 10 | 950.92 | 8644.6964
5035-Compressor Washing | 10 | 9 | 1048.7 | 843.3347
5037-Inlet bleed heat valve | 2 | 2 | 120 | 94
5039-Other compressor problems | 61 | 60 | 6871.76 | 879617.2721
5040-Fuel tanks B | 9 | 9 | 1067.4 | 3703.5897
5041-Fuel piping and valves A | 786 | 779 | 96167.28 | 1230086.4486
5042-Fuel nozzles/vanes B | 54 | 54 | 7012.97 | 153864.0603
5043-Fuel filters A | 35 | 32 | 4268.09 | 56446.9856
5044-Liquid fuel oil pump A | 36 | 36 | 3579.27 | 29014.7812
5046-Liquid fuel oil transfer/forwarding pump B | 34 | 34 | 3441.75 | 31368.3222
5047-Liquid fuel purge system A | 67 | 66 | 9276.19 | 51370.5182
5048-Gas fuel system B | 669 | 665 | 93327.59 | 1261472.3087
5049-Other fuel system problems B | 411 | 409 | 44443.86 | 534512.4218
5050-Ignition system A | 305 | 305 | 40830.05 | 199441.8629
5051-Pilot fuel piping and valves A | 90 | 89 | 10912.79 | 85391.2687
5052-Pilot fuel nozzles/vanes B | 12 | 12 | 1768.9 | 18512.3093
5053-Pilot fuel filters A | 1 | 1 | 20.2 | 10.7733
5054-Water Injection System (Gas Turbine) | 187 | 187 | 18589.71 | 209743.5744
5060-Atomizing air system B | 54 | 54 | 7539.1 | 116492.9377
5065-NOx water injection system including pumps | 26 | 26 | 2067.6 | 11486.6427
5066-NOx Steam Injection System | 5 | 5 | 978.98 | 46062.7769
5070-Combustor casing A | 14 | 14 | 2236.77 | 79971.0968
5071-Combustor liner B | 11 | 11 | 2477.2 | 152618.0891
5072-Combustor caps B | 9 | 9 | 1525.3 | 148960.7731
5073-Flame scanners B | 90 | 89 | 10540.83 | 100333.3989
5074-Flashback including instruments | 119 | 111 | 12638.17 | 446898.7176
5075-Blade Path Temperature Spread A | 268 | 261 | 39618.52 | 1455558.2241
5079-Other combustor problems B | 415 | 409 | 55080.36 | 928778.702
5080-High pressure shaft C | 12 | 12 | 925.36 | 618641.3422
5081-High pressure bearings D | 21 | 21 | 1998.2 | 84071.7562
5082-High pressure blades/buckets A | 20 | 20 | 2084.18 | 471459.7855
5083-High pressure nozzles/vanes A | 7 | 7 | 346.81 | 134847.5566
5085-Interstage gas passages - HP | 2 | 2 | 257 | 39248.1832
5088-Gas turbine cooling steam | 6 | 6 | 1920 | 20443.559
5089-Other high pressure problems B | 20 | 20 | 2480.5 | 20719.0658
5090-Low pressure shaft A | 9 | 9 | 700 | 1375.1831
5091-Low pressure bearings A | 10 | 10 | 1302.61 | 384889.8219
5092-Low pressure blades/buckets D | 6 | 6 | 403.68 | 385112.3553
5093-Low pressure nozzles/vanes B | 4 | 4 | 567 | 139635.8832
5096-Low pressure shaft seals | 1 | 1 | 1.5 | 170.025
5097-Other low pressure problems B | 6 | 6 | 241 | 128209.75
5098-Expansion joints A | 2 | 2 | 325 | 969.5832
5099-HP to LP coupling | 2 | 2 | 197 | 872.0832
5100-Chamber A | 3 | 3 | 672.9 | 157007.9748
5102-Vanes/nozzles A | 269 | 164 | 5148 | 179065.3649
5103-Silencer B | 3 | 3 | 344.9 | 131714.32
5105-Diverter Dampers B | 11 | 11 | 1038 | 29919.3665
5106-Exhaust Stack | 5 | 5 | 250 | 186417.4999
5108-High engine exhaust temperature A | 169 | 166 | 23963.58 | 285319.2159
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 166 | 166 | 21388.36 | 279404.3745
5110-Lube oil system - general | 207 | 207 | 15862.38 | 1246872.3688
5111-Lube oil pumps B | 93 | 93 | 10549.81 | 181640.0636
5112-Lube oil coolers B | 18 | 18 | 1717.1 | 17670.6902
5113-Lube oil valves/piping | 35 | 35 | 2654.25 | 40677.4798
5114-Lube oil filters | 14 | 14 | 916.83 | 13319.7998
5115-Oil vapor extractor | 12 | 12 | 960 | 14062.8997
5116-Power Augmentation System Equipment B | 22 | 22 | 1987.55 | 8320.3041
5120-Hydraulic oil system A | 195 | 195 | 20493.38 | 265937.1661
5121-Hydraulic oil system pumps | 4 | 4 | 694.57 | 3839.4241
5122-Hydraulic oil system piping/valves | 23 | 23 | 3127.78 | 43242.4071
5130-Starting system (including motor) A | 479 | 477 | 62440.43 | 1311344.6603
5140-Battery and charger system B | 20 | 20 | 2198.5 | 154932.4943
5150-Turning gear and motor C | 64 | 64 | 6142.55 | 339052.6415
5151-Load gear compartment B | 4 | 4 | 155.7 | 16703.5167
5160-Cooling and seal air system B | 142 | 135 | 19718.95 | 255702.4389
5170-Cooling water system A | 39 | 39 | 4920.43 | 122353.8626
5180-Anti-icing system A | 15 | 15 | 1336 | 24533.6996
5190-Other auxiliary system problems A | 139 | 139 | 15153.72 | 205331.8422
5200-Reduction gear B | 7 | 7 | 457.5 | 13595.9233
5201-Load shaft and bearings A | 8 | 8 | 759.86 | 173840.298
5205-Main coupling between the turbine and generator A | 3 | 3 | 199.2 | 1054.1266
5206-Gas Turbine Clutch | 21 | 21 | 1443.49 | 80894.8595
5210-Intercoolers A | 3 | 3 | 423.2 | 3700.2766
5220-Regenerators A | 1 | 1 | 53 | 12074.2833
5230-Heat shields C | 1 | 1 | 53.5 | 288.9
5240-Fire detection and extinguishing system B | 190 | 189 | 24342.92 | 324639.5118
5241-Fire in unit A | 17 | 17 | 1576.6 | 662453.9794
5245-Gas Turbine Control System - data highway | 59 | 59 | 4173.35 | 28398.646
5246-Gas Turbine Control System - hardware problems (including card failure) | 244 | 244 | 27160.3 | 278997.1185
5247-Gas Turbine Control System - internal and termination wiring | 37 | 37 | 3779.53 | 25428.5107
5248-Gas Turbine Control System - logic problems | 105 | 101 | 12910.11 | 151038.8032
5249-Gas Turbine Control System - upgrades | 33 | 33 | 4099.33 | 23610.4715
5250-Other Controls and instrumentation Problems A | 512 | 510 | 60489.9 | 737062.5016
5255-Computer | 37 | 37 | 4641.65 | 38833.9353
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 6 | 6 | 834.8 | 107461.6699
5261-Gas turbine/compressor washing | 8 | 8 | 1250.44 | 27689.1459
5270-Hot end inspection B | 5 | 5 | 548 | 341757.9332
5272-Boroscope inspection A | 13 | 13 | 1033.2 | 74629.7331
5274-General unit inspection A | 9 | 9 | 1133 | 42384.483
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 20 | 20 | 2689.98 | 394910.2332
5285-Gas turbine vibration | 188 | 187 | 17254.14 | 1576743.7995
5286-Gas Turbine lockout cause by OEM specifications | 18 | 18 | 2184.4 | 20389.9794
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 50 | 32 | 2910.9 | 12242.4602
5295-Synchronous condenser equipment A | 3 | 3 | 227.82 | 3407.8189
5298-Main gas filter | 4 | 4 | 735.44 | 7001.6204
5299-Other miscellaneous gas turbine problems | 533 | 512 | 43360.46 | 865589.7472
5401-Inlet air vanes/noozles | 11 | 11 | 607.73 | 5996.6562
5402-Inlet air filters B | 14 | 14 | 726.6 | 5215.0731
5404-Inlet air chillers A | 25 | 25 | 341 | 26783.1783
5405-Inlet air evaporative coolers A | 5 | 5 | 162.15 | 563.6974
5409-Other inlet air problems B | 9 | 9 | 345.65 | 1744.1833
5410-High pressure shaft B | 1 | 1 | 35 | 141.1667
5411-High pressure bearings B | 1 | 1 | 45 | 10.5
5412-High pressure blades/buckets C | 9 | 9 | 358.52 | 274560.9254
5413-Other high pressure problems D | 5 | 5 | 203.6 | 5457.8533
5414-Compressor diaphragms/vanes | 13 | 13 | 719.8 | 339636.7216
5420-Low pressure shaft C | 1 | 1 | 192 | 220.8
5429-Other low pressure problems D | 6 | 6 | 395.9 | 2098.9699
5436-Compressor shaft & bearings two shaft machines | 1 | 1 | 50 | 1419.1666
5439-Jet engine other compressor problems | 21 | 21 | 900.46 | 6329.1778
5440-Fuel tanks A | 1 | 1 | 56.5 | 209.9916
5441-Fuel piping and valves B | 155 | 154 | 6116.3 | 65843.5712
5442-Fuel nozzles/vanes A | 14 | 13 | 747.4 | 17017.153
5443-Fuel filters B | 11 | 11 | 397.61 | 3134.858
5444-Liquid fuel oil pump B | 29 | 29 | 1234.4 | 31633.8997
5445-Liquid fuel oil transfer/forwarding pump A | 33 | 33 | 1114.13 | 5289.3369
5446-Liquid fuel purge system B | 8 | 8 | 393.4 | 3256.2882
5447-Gas fuel system A | 146 | 146 | 6220.25 | 82866.4396
5449-Other fuel system problems A | 105 | 104 | 4782.22 | 205393.0094
5450-Ignition system B | 53 | 53 | 2246.52 | 57884.0375
5451-Pilot fuel piping and valves B | 5 | 5 | 206.9 | 798.9649
5452-Pilot fuel nozzles/vanes A | 1 | 1 | 186.52 | 1234.1405
5454-Water injection system (Jet Engine) | 110 | 110 | 4144.3 | 46028.8189
5460-Atomizing air system A | 21 | 21 | 1117 | 29766.6663
5471-Combustor liner A | 1 | 1 | 21 | 17535
5472-Combustor caps A | 2 | 2 | 81.1 | 5555.4683
5473-Flame scanners A | 30 | 29 | 2011.59 | 12189.8219
5475-Blade Path Temperature Spread B | 47 | 47 | 5936.8 | 75008.7745
5479-Other combustor problems A | 33 | 33 | 2451.06 | 73860.8537
5481-High pressure bearings A | 4 | 4 | 181.1 | 141253.8449
5482-High pressure blades/buckets D | 9 | 9 | 376.3 | 411307.9583
5485-Interstage gas passages | 4 | 4 | 228.4 | 5766.81
5486-High pressure shaft seals B | 2 | 2 | 302.61 | 9843.9337
5489-Other high pressure problems C | 3 | 3 | 117.44 | 43965.942
5490-Low pressure shaft B | 1 | 1 | 32 | 63142.4
5492-Low pressure blades/buckets B | 1 | 1 | 46 | 16.8666
5493-Low pressure nozzles/vanes A | 2 | 2 | 86 | 47527.2666
5497-Other low pressure problems C | 4 | 4 | 178 | 1005.7333
5500-Chamber B | 2 | 2 | 67 | 15201.1833
5505-Diverter Dampers A | 1 | 1 | 25 | 2.9167
5508-High engine exhaust temperature B | 41 | 41 | 1707.6 | 5224.2194
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 13 | 13 | 695.79 | 418410.9517
5510-Lube oil system A | 224 | 220 | 9564.24 | 249326.1705
5516-Power Augmentation System Equipment A | 10 | 10 | 156.5 | 649.0916
5520-Hydraulic oil system B | 30 | 30 | 1435.92 | 14327.1563
5530-Starting system (including motor) B | 108 | 108 | 3595.83 | 164168.1741
5540-Battery and charger system A | 3 | 3 | 137 | 645.8
5550-Turning gear and motor B | 5 | 5 | 228.6 | 8450.65
5560-Cooling and seal air system A | 30 | 30 | 1183.61 | 8916.2495
5570-Cooling water system B | 27 | 27 | 319.5 | 300.6999
5580-Anti-icing system B | 9 | 9 | 409 | 1369.6498
5590-Other auxiliary system problems B | 116 | 115 | 4425.76 | 89666.3866
5605-Main coupling between the turbine and generator B | 4 | 4 | 182.4 | 512.2399
5606-Jet Engine Clutch | 4 | 4 | 183.7 | 8269.4666
5640-Fire detection and extinguishing system A | 38 | 38 | 1406.85 | 27139.3629
5641-Fire in unit B | 4 | 4 | 129 | 85975.2749
5645-Jet Engine Control System - data highway | 22 | 22 | 1125.95 | 6941.0405
5646-Jet Engine Control System - hardware problems (including card failure) | 89 | 89 | 3422.71 | 51921.1567
5647-Jet Engine Control System - internal and termination wiring | 21 | 20 | 963.2 | 7834.7514
5648-Jet Engine Control System - logic problems | 48 | 46 | 2087.52 | 16241.546
5649-Jet Engine Control System - upgrades | 2 | 2 | 95.2 | 946.9333
5650-Other Controls and instrumentation Problems B | 188 | 171 | 7595.03 | 42481.0468
5660-Major overhaul (use for non-specific overhaul only; see page B-1) C | 3 | 3 | 179.9 | 111370.5749
5661-Engine/compressor washing | 1 | 1 | 48 | 106.4
5662-Engine exchange | 15 | 15 | 471.9 | 30113.4148
5665-Engine shafts and bearings | 5 | 5 | 105 | 77603.4166
5672-Boroscope inspection B | 5 | 5 | 329.51 | 7248.4784
5674-General unit inspection B | 13 | 13 | 785.55 | 3229.8748
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 61 | 61 | 2285.34 | 10768.026
5685-Engine vibration | 149 | 143 | 5837.55 | 74664.1376
5686-Jet Engine lockout cause by OEM specifications | 6 | 4 | 189.2 | 10070.6
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 12 | 10 | 766.56 | 833.093
5695-Synchronous condenser equipment B | 2 | 2 | 34 | 64.0333
5699-Other miscellaneous jet engine problems | 174 | 174 | 7055.13 | 555698.2804
5700-Drive shaft and bearings | 8 | 8 | 255.8 | 27353.185
5710-Cylinders | 13 | 13 | 119.68 | 11849.134
5711-Cylinder heads | 8 | 7 | 85 | 198.3666
5720-Pistons | 7 | 7 | 56 | 1458.0666
5730-Intake valves | 1 | 1 | 27 | 15.3
5731-Exhaust valves | 2 | 2 | 7.31 | 62.0522
5740-Turbo charger | 4 | 4 | 98.7 | 8081.64
5799-Other engine problems | 6 | 6 | 51.87 | 3093.4136
5800-Lube oil system C | 14 | 14 | 109.69 | 149.0496
5805-Cooling system | 5 | 5 | 45.41 | 647.1176
5815-Fuel system | 11 | 11 | 81.79 | 504.7195
5820-Start system | 11 | 11 | 75.61 | 1153.284
5830-Air filter system | 1 | 1 | 2.57 | 73.8875
5849-Other engine auxiliaries problems | 2 | 2 | 22 | 11.9
5855-Engine control system | 20 | 19 | 150.11 | 385.1633
5865-Synchronization system | 1 | 1 | 2.57 | 5241.258
5870-Other engine control problems | 6 | 6 | 61.97 | 78.3365
5880-Internal Combustion/Reciprocating Engines unit overhaul | 4 | 4 | 36 | 30825
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 6 | 6 | 17.59 | 3.8835
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 45 | 45 | 7396.36 | 54989.9686
6005-HP Evaporator tubes | 17 | 17 | 2824 | 305316.434
6006-IP Evaporator tubes | 2 | 2 | 307 | 79692.6832
6007-LP Evaporator tubes | 7 | 7 | 1272 | 87562.5496
6010-HP superheater | 22 | 22 | 3897.6 | 197933.1591
6011-HP reheater | 8 | 8 | 940 | 99865.5162
6012-HP economizer | 18 | 18 | 2094.66 | 370304.4658
6021-IP reheater | 4 | 4 | 444.32 | 27192.86
6022-IP economizer | 7 | 7 | 1183.24 | 23666.1396
6032-LP economizer | 8 | 8 | 1539.85 | 30527.7411
6090-Other HRSG tube Problems | 16 | 16 | 2661.9 | 142239.4129
6100-Steam turbine to gas turbine coupling. For additional codes; use Fossil Steam Cause Codes 4000 to 4499. | 43 | 43 | 6343.72 | 42839.337
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 32 | 31 | 5776.67 | 186239.3845
6111-HP steam relief/safety valves | 8 | 8 | 500 | 28284.1333
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 71 | 69 | 12350.92 | 176990.5511
6113-Other HP steam system problems | 17 | 17 | 2167.04 | 17898.9344
6114-HP steam isolation/boundary valves | 6 | 6 | 851.3 | 15285.9115
6120-IP steam piping up to turbine stop valves - Between 200 & 600 PSIG (see 0790 for piping supports) | 3 | 3 | 569.5 | 1443.6831
6121-IP steam relief/safety valves | 7 | 7 | 1317.5 | 13427.7078
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 13 | 12 | 2262.76 | 27166.4889
6123-Other IP steam system problems | 11 | 11 | 1952.1 | 24385.7843
6130-LP steam piping up to turbine stop valves - Less than 200 PSIG (see 0790 for piping supports) | 4 | 4 | 512.9 | 8057.8415
6131-LP steam relief/safety valves | 4 | 4 | 611 | 2387.9915
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 4 | 4 | 435.7 | 38853.1649
6133-Other LP steam system problems | 8 | 8 | 1031.73 | 28421.5183
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 31 | 31 | 4951.73 | 174768.205
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 13 | 13 | 2056.14 | 67837.0405
6141-HP Desuperheater/attemperator valves | 22 | 22 | 3289.6 | 179341.3589
6142-HP Desuperheater/attemperator spray nozzles | 2 | 2 | 267 | 6339.95
6143-HP Desuperheater/attemperator drums | 6 | 6 | 1021 | 12474.216
6144-Other HP desuperheater/attemperator problems | 4 | 4 | 673 | 576.2998
6145-IP Desuperheater/attemperator piping - Between 200-600 PSIG | 1 | 1 | 148.8 | 5860.24
6146-IP Desuperheater/attemperator valves | 15 | 15 | 2523.8 | 12985.9611
6148-IP Desuperheater/attemperator drums | 1 | 1 | 113 | 35.7833
6149-Other IP desuperheater/attemperator problems | 2 | 2 | 310 | 687.1665
6151-LP Desuperheater/attemperator valves | 1 | 1 | 138 | 524.4
6154-Other LP desuperheater/attemperator problems | 1 | 1 | 131 | 264.1832
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 4 | 4 | 654 | 3695.1
6161-HP Startup bypass system valves | 35 | 35 | 7131.93 | 264494.2505
6163-Other HP startup bypass system problems | 1 | 1 | 612 | 724.1998
6164-HP Startup bypass instrumentation and controls | 33 | 33 | 6134.73 | 126482.8428
6170-IP Startup bypass system piping (including drain lines up to heaters or condenser) - Between 200-600 PSIG | 4 | 4 | 786.5 | 13187.7999
6171-IP Startup bypass system valves | 29 | 29 | 5025.93 | 13142.3241
6173-Other IP startup bypass system problems | 5 | 5 | 576 | 1368.1665
6174-IP Startup bypass instrumentation and controls | 26 | 26 | 4823.6 | 71986.9086
6181-LP Startup bypass system valves | 4 | 4 | 808.4 | 786.0332
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 78 | 78 | 13033.54 | 119942.0981
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 224 | 222 | 31809.11 | 498816.5487
6399-Other coal gasification equipment problems | 1 | 1 | 220 | 264
6410-Steam wells/steam field piping problems | 15 | 15 | 94 | 1966.9333
6415-Low steam pressure | 2 | 2 | 8.84 | 139.68
6420-Condensate reinjection system | 1 | 1 | 18 | 5.7
6440-H2S abatement system problems ? general | 3 | 3 | 66 | 99.9333
6499-Geothermal | 121 | 114 | 1080.25 | 31143.4812
7000-Shaft B | 4 | 4 | 105.98 | 11535.718
7001-Shaft packing | 19 | 19 | 1102.36 | 62411.954
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 45 | 45 | 2865.22 | 129744.9935
7007-Bearings A | 34 | 34 | 2853.82 | 1306953.6338
7008-Bearing cooling system B | 39 | 36 | 1691.75 | 27797.9409
7009-Bearing Oil System | 48 | 48 | 4858.93 | 59533.8493
7010-Runner cavitation damage | 4 | 4 | 219.59 | 17068.9311
7011-Other runner problems | 107 | 105 | 857.37 | 1456246.3621
7014-Blade or bucket cracking | 2 | 2 | 76.55 | 117886.655
7020-Nozzle assembly | 5 | 5 | 192.5 | 4884.7633
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 16 | 16 | 868.57 | 145718.2025
7040-Turbine overhaul | 1 | 1 | 62.5 | 101.0416
7050-Turbine governor | 271 | 269 | 20657.38 | 644420.0355
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 68 | 68 | 3749.76 | 342280.86
7053-Governor Oil System | 84 | 84 | 7021.43 | 151814.9342
7099-Other turbine problems | 195 | 185 | 7690.18 | 1201382.9832
7100-Upper reservoir dams and dikes | 6 | 6 | 217.65 | 1839.1383
7101-Lower reservoir dams and dikes | 40 | 39 | 1544.6 | 157909.8861
7110-Intake channel or flume (including trash racks) | 119 | 112 | 5388.99 | 43927.3902
7111-Intake tunnel | 34 | 34 | 4421.41 | 66646.2247
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 68 | 66 | 888.87 | 34147.1573
7120-Headgates | 27 | 27 | 1391.82 | 30080.2087
7121-Shutoff valves | 29 | 29 | 3490.27 | 46168.0123
7123-Shutoff valve bypass line and valve | 8 | 8 | 1023.56 | 13694.0057
7124-Penstock | 18 | 18 | 1281.78 | 29814.7529
7130-Spiral case | 6 | 6 | 519.7 | 8417.3749
7140-Wicket gate assembly | 27 | 27 | 1841.18 | 468467.636
7141-Wicket gate operating mechanism or positioner | 24 | 24 | 2197.11 | 13927.1619
7142-Wicket gate shear pin | 157 | 157 | 11358.69 | 263526.4727
7160-Pressure regulating valve | 3 | 3 | 150.14 | 475.9316
7161-Pressure regulating valve operator or positioner | 16 | 15 | 532.3 | 2848.1215
7162-Relief valve and vacuum breakers | 6 | 6 | 419.93 | 52377.4632
7170-Draft tube | 23 | 22 | 1473.01 | 39579.8162
7180-Tailrace | 23 | 23 | 1397 | 36832.3625
7181-Tail water depressing equipment | 9 | 9 | 461.23 | 4626.7516
7190-Dewatering and rewatering equipment | 14 | 14 | 812.16 | 14532.6682
7191-Equalizing line | 1 | 1 | 345 | 345
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 222 | 218 | 3357.44 | 161351.6655
7200-Major overhaul (use for non-specific overhaul only; see page B-1) B | 1 | 1 | 23 | 82087
7201-Inspection A | 5 | 5 | 329.02 | 1145.9099
7210-Canals (including siphons; radial gates; and spills) | 7 | 7 | 276.56 | 10485.4525
7220-Unit out of service due to common penstock with unit under repair | 1 | 1 | 195 | 1628.25
7230-Pony motor (pumped storage units only) | 1 | 1 | 340 | 1071
7240-Powerhouse Substructure | 3 | 3 | 499.81 | 1146.7977
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 67 | 65 | 2069.08 | 149659.1566
7800-Couplings | 1 | 1 | 38 | 588.3667
7810-Shaft A | 1 | 1 | 29 | 1215.5833
7820-Bearings B | 3 | 3 | 105 | 356567.9166
7860-Nozzles/vanes | 2 | 2 | 85 | 57385.8
7880-Exhaust diffusers | 3 | 3 | 311.28 | 57338.3332
7890-Seal oil system and seals B | 5 | 5 | 432 | 6190.8831
7910-Outer exhaust casing | 2 | 2 | 66.24 | 5891.3733
7920-Lube oil system B | 15 | 15 | 549.5 | 55196.6832
7930-Controls and instrumentation A | 18 | 18 | 1209.27 | 105303.9546
7960-Other expander turbine problems | 16 | 16 | 870.5 | 288203.058
8000-Chemical feed storage; mill feeders; and conveyors | 35 | 35 | 6512.34 | 23372.6616
8006-Weigh feeders | 11 | 11 | 1040.9 | 10546.1831
8010-Crushers/mills | 74 | 73 | 10910.43 | 125268.9146
8020-Mill slurry tanks supply problems | 6 | 6 | 2031 | 9889.6657
8040-Slurry transfer pumps and motors | 7 | 7 | 851.13 | 2160.4197
8050-Chemical unavailability | 3 | 3 | 170 | 611.1666
8099-Other chemical supply problems | 23 | 23 | 3283 | 29822.9161
8100-Scrubber/absorber tower or module | 79 | 79 | 7610.7 | 118907.4027
8110-Spray nozzles | 22 | 22 | 3046.45 | 100796.7799
8120-Spray pumps and motors | 12 | 12 | 1441.05 | 3599.4714
8125-Scrubber recycle (liquid) pumps | 29 | 29 | 3112.25 | 34280.749
8127-Scrubber recycle (liquid) pump motors | 9 | 9 | 1291 | 47661.3997
8130-Recirculation tanks including agitators | 6 | 6 | 701 | 18226.8165
8140-Reaction tanks including agitators | 3 | 3 | 460 | 15315.8498
8150-Tubes | 5 | 5 | 810.3 | 29385.5848
8160-Mist eliminators/demisters and washdown | 29 | 29 | 2781 | 202364.366
8199-Other scrubber problems | 89 | 89 | 11819.14 | 97618.2645
8200-Piping | 31 | 31 | 7042.29 | 212021.6212
8210-Valves | 32 | 32 | 3329.4 | 10067.7604
8220-Strainers or filters | 12 | 12 | 2145 | 9487.9996
8230-Ducting | 13 | 13 | 1801.72 | 14141.8231
8235-Demister | 16 | 16 | 605 | 99040.4365
8240-Bypass dampers | 9 | 9 | 769 | 2378.5831
8250-Dampers other than bypass | 9 | 9 | 1468.58 | 32752.264
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 163 | 162 | 17854.25 | 269262.32
8261-Scrubber booster I.D. fan drive | 14 | 14 | 2159.03 | 172875.2701
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 92 | 76 | 12072.06 | 335642.4305
8264-Scrubber booster I.D. fan blades (fan specific to the scrubber) | 12 | 12 | 881.25 | 3180.6622
8265-Scrubber ID fan dampers | 2 | 2 | 115 | 6182
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 7 | 7 | 1513 | 28666.8663
8271-Scrubber booster F.D. fan drive | 11 | 11 | 1612.9 | 3473.3562
8272-Scrubber booster F.D. fan vibration (fan specific to the scrubber) | 2 | 2 | 50 | 16.6667
8280-Reagent feed piping | 13 | 13 | 1607.8 | 3720.576
8299-Other piping; ducting; damper; and fan problems | 50 | 50 | 3165.5 | 66951.4241
8300-Waste disposal/recovery tanks | 1 | 1 | 7 | 127.1667
8325-Ash disposal problems | 1 | 1 | 175 | 320.8333
8330-Dewatering equipment (thickener; centrifuge; etc.) | 8 | 8 | 1606.72 | 49314.5368
8399-Solids conveying and mixing system problems | 5 | 5 | 1875 | 84993.3661
8400-Scrubber gas discharge reheaters - general | 3 | 3 | 274 | 5808.3665
8404-Scrubber gas discharge reheaters - tube leaks | 1 | 1 | 111 | 3111.7
8410-Scrubber instruments and controls | 20 | 20 | 5973 | 33285.448
8415-Liquid level controls | 16 | 16 | 1885 | 32777.1663
8425-Miscellaneous mechanical failures | 6 | 6 | 410.51 | 1285.9941
8426-Miscellaneous electrical failures | 9 | 9 | 354.56 | 1764.2802
8430-Stack damage related to scrubber system | 5 | 5 | 454 | 7695.55
8450-Inspection | 1 | 1 | 87 | 3295.85
8460-Testing | 14 | 14 | 1924.78 | 12110.53
8470-SO2 monitor | 8 | 8 | 200 | 1850.3332
8499-Other miscellaneous wet scrubber problems | 164 | 164 | 7403.1 | 154568.6225
8500-Slurry storage and feed tanks | 9 | 9 | 1053 | 6214.4328
8501-Reagent storage; feed bins; and conveyors | 2 | 2 | 68.47 | 585.26
8502-Weigh feeders | 2 | 2 | 497 | 1133.05
8504-Mills/slakers | 5 | 5 | 766 | 3076.5
8505-Scalping screens | 1 | 1 | 60 | 9
8506-Slurry pipelines | 16 | 16 | 1589.6 | 4832.4213
8507-Reagent uploading and transfer systems | 2 | 2 | 171 | 788.9833
8508-Reagent unavailability | 4 | 4 | 388.61 | 2478.2921
8510-Slurry mixers and agitators | 3 | 3 | 287.22 | 5259.1174
8520-Slurry transfer pumps and motors | 15 | 15 | 997 | 2160.7871
8521-Reagent/slurry problems | 9 | 9 | 1151.3 | 9853.3616
8522-Piping | 2 | 2 | 222.72 | 1142.9586
8523-Valves | 1 | 1 | 21 | 154.35
8524-Strainers or filters | 4 | 4 | 268 | 1312.9999
8525-Ducting | 2 | 2 | 31.37 | 261.901
8526-Dampers | 3 | 3 | 69 | 38.8
8527-Other piping; ducting; and damper problems | 6 | 6 | 255.83 | 665.89
8528-Dry scrubber instruments and controls | 7 | 7 | 386.86 | 5837.7388
8529-Gas dispersers | 1 | 1 | 39 | 1055.6
8530-Spray towers | 8 | 8 | 531.5 | 311525.6414
8531-Spray machine/atomizer | 97 | 97 | 6862.49 | 59265.4374
8532-Spray machine/atomizer motors | 3 | 3 | 309 | 2829.2832
8533-Spray machine/atomizer lubrication systems | 14 | 14 | 796 | 2642.0497
8534-Spray machine/atomizer vibration problems | 29 | 29 | 2012.22 | 8195.7436
8535-Fly ash conveyors | 5 | 5 | 290.1 | 5960.3015
8538-Recycle storage and feed tanks including agitators | 7 | 7 | 543 | 3181.8665
8539-Recycle slurry transfer pumps | 4 | 4 | 253 | 849.5166
8540-Waste disposal | 5 | 5 | 74.57 | 1342.87
8542-Recycle feed bins aeration systems | 4 | 4 | 35.59 | 604.932
8544-Mechanical failures | 42 | 42 | 2391.42 | 118253.4825
8545-Electrical failures | 8 | 8 | 740.34 | 11934.3001
8547-Inspection | 2 | 2 | 60.75 | 2160.75
8548-Testing | 1 | 1 | 50 | 130.8333
8549-Other dry scrubber problems | 50 | 50 | 3245 | 42181.824
8550-Electrostatic precipitator fouling | 421 | 411 | 34119.59 | 2127739.0806
8551-Electrostatic precipitator field out of service | 1018 | 1005 | 44022.75 | 577381.8142
8560-Electrostatic precipitator problems | 356 | 355 | 24603.07 | 378237.4981
8570-Mechanical precipitator fouling | 1 | 1 | 40 | 94.6666
8580-Mechanical precipitator problems | 5 | 5 | 171 | 1631.0666
8590-Other precipitator problems | 74 | 73 | 5846.26 | 122549.3346
8600-Flue gas additives (furnace injection) | 48 | 48 | 4175.8 | 54948.7267
8601-SO3 mitigation | 25 | 25 | 3095 | 26755.9957
8650-Baghouse systems; general | 558 | 557 | 27607.24 | 546357.3844
8651-Bag failures and rebagging | 191 | 189 | 8474.86 | 142226.686
8652-Shakers and rappers | 6 | 6 | 158.56 | 297.4679
8654-Baghouse booster fans and motors | 38 | 38 | 2986.4 | 28725.2959
8655-Structural duct work and dampers | 20 | 20 | 2239.4 | 107180.6965
8656-Controls and instrumentation B | 68 | 65 | 3202 | 64820.0489
8657-Ash handling system and hoppers | 111 | 111 | 11580.43 | 334141.8534
8658-Slurry system from precipitators | 6 | 6 | 920 | 3609.4996
8670-Emission monitors (other than CEMS) A | 34 | 34 | 5752.93 | 38102.2421
8699-Other miscellaneous pollution control equipment problems | 168 | 168 | 11230.42 | 121179.312
8700-CEMS Certification and Recertification | 43 | 43 | 5366.9 | 22111.194
8710-SO2 analyzer problems | 7 | 7 | 656.69 | 840.7565
8720-NOx analyzer problems | 65 | 65 | 4661.83 | 140832.5641
8730-CO analyzer problems | 18 | 18 | 1066.7 | 113728.1496
8740-CO2 analyzer problems | 6 | 6 | 514 | 22418.9333
8750-O2 analyzer problems | 16 | 16 | 1492.2 | 80148.5912
8760-Opacity monitor problems | 54 | 54 | 4758.75 | 90061.8648
8770-Flow monitor problems | 17 | 17 | 2341.11 | 41877.1878
8780-Data acquisition system problems | 20 | 20 | 2080.7 | 19956.9827
8790-Miscellaneous CEMS problems | 102 | 102 | 8975.29 | 157376.8929
8800-SNCR NOx Reagent | 3 | 3 | 105.9 | 912.785
8801-SNCR NOx Carrier gas | 1 | 1 | 31 | 290.8833
8802-SNCR NOx Control system | 17 | 17 | 1383.62 | 8422.8655
8803-Sncr Performance Testing | 7 | 7 | 36.9 | 459.0833
8809-Other SNCR NOx problems | 30 | 30 | 1298.18 | 32763.196
8810-SCR NOx Reactor | 1 | 1 | 125.8 | 255.7933
8812-SCR NOxCatalyst | 18 | 18 | 1278.4 | 35605.6896
8813-SCR NOx Injection grid piping/valves | 26 | 26 | 2010.5 | 36151.3061
8814-SCR NOx Catalyst support material | 2 | 2 | 20 | 9.1667
8815-SCR NOx Soot blowers | 2 | 2 | 314 | 3452
8816-SCR NOx Plugging | 42 | 42 | 3664.66 | 133254.9593
8817-SCR NOx Control system | 64 | 63 | 4994.84 | 19590.2099
8820-SCR NOx Ammonia injection grid piping/valves | 36 | 36 | 6099.07 | 61698.2241
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 46 | 46 | 7008.6 | 81345.786
8822-SCR NOx Ammonia air blowers | 13 | 13 | 644.33 | 5051.1864
8823-SCR NOx Other ammonia system problems | 107 | 106 | 7662.82 | 40512.2004
8825-Other SCR NOx problems | 60 | 60 | 5493.08 | 51982.1612
8830-CAH NOx Active catalyst | 5 | 5 | 106 | 49.1333
8835-CAH NOx Other CAH problems | 2 | 2 | 96 | 417.7
8840-CO Active catalyst | 35 | 25 | 935 | 656.0163
8842-CO Plugging | 1 | 1 | 7 | 107.9167
8845-Other CO reduction problems | 113 | 112 | 4091.15 | 17726.647
9000-Flood | 107 | 107 | 7266.2 | 2991150.2224
9010-Fire; not related to a specific component | 21 | 19 | 2404.29 | 662562.5125
9020-Lightning | 242 | 242 | 33704.65 | 848725.9878
9025-Geomagnetic disturbance | 1 | 1 | 220 | 667.3333
9030-Earthquake | 6 | 6 | 555 | 1233.9998
9035-Hurricane | 29 | 29 | 1334 | 1324825.2995
9036-Storms (ice; snow; etc) | 90 | 90 | 12668.4 | 683285.9852
9040-Other catastrophe | 21 | 21 | 3161.59 | 247930.1591
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 662 | 656 | 71431.86 | 3192526.8712
9131-Lack of fuel: Contract or Tariff allows for interruption | 1254 | 1203 | 94485.54 | 6931450.4985
9134-Fuel conservation | 275 | 271 | 19133.69 | 606670.3615
9135-Lack of water (hydro) | 2392 | 2186 | 35670.56 | 1709486.7505
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 32 | 32 | 2435.62 | 27745.5799
9137-Ground water or other water supply problems | 15 | 15 | 1862.1 | 251665.3927
9150-Labor strikes company-wide problems or strikes outside the company's jurisdiction such as manufacturers (delaying repairs) or transportation (fuel supply) problems. | 3 | 3 | 55.32 | 20238.822
9160-Other economic problems | 33 | 33 | 3429.12 | 549077.452
9180-Economic (for internal use at plants only) | 6 | 6 | 210.48 | 74115.0399
9200-High ash content | 82 | 82 | 3690.36 | 33899.3229
9201-High ash content ? (not outside management control) | 185 | 185 | 14203 | 461778.9133
9205-Poor quality natural gas fuel; low heat content | 12 | 12 | 271.91 | 5375.1066
9210-Low grindability | 21 | 21 | 1382 | 14805.1997
9211-Low grindability (not outside management control) | 25 | 25 | 1772.22 | 30002.492
9220-High sulfur content | 8 | 8 | 293.91 | 61120.2632
9221-High sulfur content ? (not outside management control) | 26 | 26 | 2263 | 34427.8327
9230-High vanadium content | 7 | 7 | 517.1 | 3415.6048
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 1084 | 1071 | 32812.8 | 1174019.8277
9251-Low Btu Coal From Contract For Low Btu Coal | 230 | 229 | 7200.04 | 168607.712
9260-Low Btu oil | 2 | 2 | 71.91 | 3195.02
9270-Wet coal | 1886 | 1860 | 139694.7 | 1505035.0195
9271-Wet coal (not outside management control) | 521 | 521 | 38073.88 | 527663.5034
9280-Frozen coal | 99 | 98 | 7921.07 | 51797.6332
9281-Frozen coal (not outside management control) | 86 | 86 | 10399.64 | 174423.3661
9290-Other fuel quality problems | 878 | 860 | 66050.33 | 494771.9474
9291-Other fuel quality problems (not outside management control) | 541 | 526 | 18804.45 | 638395.1425
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 1625 | 1603 | 105573.22 | 1985519.307
9305-Ash disposal problem | 5 | 5 | 182 | 1767.9166
9310-Operator training | 13 | 13 | 923.63 | 244747.4386
9320-Other miscellaneous external problems | 1216 | 1111 | 59339.7 | 2154018.3283
9340-Synchronous Condenser Operation | 1 | 1 | 120 | 330
9345-Pumping Operations | 1 | 1 | 40.85 | 40.85
9350-Public Safety/River Rescue | 26 | 26 | 499 | 3286.4833
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 16 | 16 | 1674.7 | 38778.1144
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 75 | 53 | 5399.62 | 1813753.54
9600-SO2 stack emissions (fossil) | 228 | 220 | 12949.1 | 138982.2852
9603-SO2 stack emissions (gas turbine) | 1 | 1 | 53 | 341.85
9604-SO2 stack emissions (jet engines) | 1 | 1 | 52 | 26
9610-NOx stack emissions (fossil) | 249 | 238 | 14309.98 | 349685.9491
9613-NOx stack emissions (gas turbine) | 74 | 73 | 7830.2 | 224724.5685
9614-NOx stack emissions (jet engines) | 37 | 33 | 1445.4 | 12556.8079
9615-NOx stack emissions (Internal Combustion/Reciprocating Engines) | 3 | 3 | 22.64 | 1976.8592
9616-CO stack emissions | 153 | 126 | 3918.77 | 102943.8383
9620-Particulate stack emissions (fossil) | 177 | 177 | 15415.14 | 366527.2579
9623-Particulate stack emissions (gas turbine) | 3 | 3 | 142.02 | 18710.431
9630-Opacity (fossil) | 2363 | 2343 | 115506.16 | 1933432.3064
9650-Other stack or exhaust emissions (fossil) | 167 | 166 | 9100.52 | 211821.8785
9653-Other stack or exhaust emissions (gas turbine) | 36 | 36 | 2285.91 | 39352.4583
9654-Other stack or exhaust emissions (jet engines) | 11 | 11 | 712.3 | 3330.7097
9655-Other stack or exhaust emissions (Internal Combustion/Reciprocating Engines) | 7 | 7 | 69.81 | 623.6896
9656-Other stack or exhaust emissions testing - fossil | 28 | 28 | 1688.93 | 11600.7564
9657-Other stack or exhaust emissions testing - gas turbine | 4 | 4 | 14.9 | 3994.9383
9658-Other stack or exhaust emissions testing - jet engines | 1 | 1 | 28.9 | 89.59
9660-Thermal discharge limits (fossil and nuclear) | 126 | 126 | 5568.87 | 108014.4035
9663-Thermal discharge limits (gas turbine) | 1 | 1 | 15.1 | 626.65
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 61 | 57 | 2169.64 | 48385.6616
9693-Other miscellaneous operational environmental limits (gas turbines) | 14 | 14 | 1243.02 | 4896.7253
9694-Other miscellaneous operational environmental limits (jet engines) | 11 | 11 | 261.05 | 1496.4021
9695-Other miscellaneous operational environmental limits (Internal Combustion/Reciprocating Engines) | 5 | 5 | 19.36 | 13548.7233
9696-Other miscellaneous operational environmental limits (hydro and PS) | 9 | 9 | 221.68 | 3780.1273
9720-Other safety problems | 54 | 54 | 4436.41 | 466441.0446
9900-Operator error | 690 | 682 | 159523.13 | 1449709.9248
9910-Maintenance personnel error | 213 | 213 | 43284.6 | 524980.2532
9920-Contractor error | 78 | 78 | 15511.97 | 606316.0058
9930-Operating procedure error | 84 | 82 | 9663.25 | 28045.2507
9940-Maintenance procdure error | 46 | 46 | 5524.58 | 91622.6203
9950-Contractor procedure error | 14 | 14 | 2251.51 | 38798.1001
9960-Staff shortage | 20 | 20 | 2443.95 | 1077539.219
9997-NERC Reliability Standards requirements | 5 | 5 | 222.53 | 207752.8394
9998-Black Start testing | 10 | 10 | 926.5 | 2027.3998
9999-Total unit performance testing (use appropriate codes for individual component testing) | 304 | 299 | 10446.21 | 2052478.6068
Total Result | 90265 | 88078 | 9395543.84 | 369883338.6042

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 418.418 | 34.58 | 1 | 1 | 0010-Thaw shed failure or fire | U1-Forced - Immediate | 862-CoG steam units
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6063.1999 | 156 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255 | 85 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 675 | 135 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1450 | 145 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12825.9998 | 330 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 645.3333 | 88 | 2 | 2 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 449.1666 | 110 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 630.8 | 152 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1995 | 210 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.5 | 25 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 682 | 155 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 19.5 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 182 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 786.5 | 39 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 247 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 30.9833 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 55.25 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 165.75 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 35.75 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 469.0833 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 6.5 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 231.8333 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 251.55 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 113.75 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 182 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 37.9167 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 52 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 170.0833 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 234 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 94.25 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 23.8333 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 58.5 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 114.8333 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1197.7333 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 316.6666 | 100 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 248.2 | 51 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1605.65 | 51 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 314.1666 | 58 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 11.3667 | 11 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 188.5833 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 143.9833 | 53 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 103.7 | 51 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 5030.3 | 51 | 1 | 1 | 0024-Rotary plow | U2-Forced - Delayed | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 732.5333 | 16 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 209.95 | 51 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 233.9333 | 58 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 74.75 | 23 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 143.5 | 41 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2275.25 | 57 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 17.7833 | 11 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 47.3666 | 58 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 200.6666 | 43 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 696 | 16 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 130.7166 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33433.3332 | 400 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 45.9833 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 749.1666 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 100.75 | 13 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 800-Miscellaneous
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1032.6333 | 26 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 800-Miscellaneous
0026 | Dust suppression system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1925 | 275 | 1 | 1 | 0026-Dust suppression system | D2-Forced - Delayed | 100-Fossil-Steam
0026 | Dust suppression system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 16.6667 | 12.5 | 1 | 1 | 0026-Dust suppression system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 791.7 | 203 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 515.9 | 294.8 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 680.55 | 104.7 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.9166 | 151 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1550.9999 | 180 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 136 | 136 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 323.6333 | 9.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 431.7917 | 21.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 344.65 | 113 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 379.95 | 25.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 574.1665 | 265 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1127 | 230 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 126.225 | 25.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.75 | 21 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 151.2833 | 14.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 4527.1333 | 44.5 | 1 | 1 | 0028-Dust collection system | U1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1171.4665 | 368 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.35 | 19 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.7 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.6333 | 106 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 215.9332 | 164 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 309.8332 | 143 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 497.9332 | 388 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 646.7333 | 178 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1167.25 | 203 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2384.3332 | 460 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2713.3332 | 370 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2793.9998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4857.6 | 384 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.6167 | 29 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59.2 | 74 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.25 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 175.2666 | 239 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 202.9999 | 174 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 504.1665 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 783.3333 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1060 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1720 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5356.8 | 288 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.4333 | 17.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.3333 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.975 | 31.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 188 | 94 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198.55 | 36.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 242.25 | 95 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 696.0416 | 32.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 822.5 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1015.2 | 141 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1235.99 | 176.57 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4734.9999 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.4 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 74 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2194.0675 | 302.63 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 11.0667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 348 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 21.9333 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 24.0667 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 51.3 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 662.3666 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 89.3255 | 4.47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1555.7 | 141 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2791.3332 | 316 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 960 | 240 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108 | 108 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164 | 164 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1107.7 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1097.9998 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1499.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2101.6666 | 260 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9115.4333 | 122 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 1587.8 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.3333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.0665 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 157.5 | 315 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 293.3333 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300.8332 | 475 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 451.25 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 537.3333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 968.5 | 149 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1372.6664 | 355 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2754.96 | 114.79 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168.75 | 27 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 367.6332 | 538 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 446.55 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 588 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 620 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 738.0999 | 183 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 800 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1611.2998 | 369 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2484 | 69 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.8145 | 19.47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19 | 19 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.7333 | 71.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.3332 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 707.1831 | 281 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1058.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1343.3333 | 124 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1605.3332 | 224 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2030.3998 | 324 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2188.8999 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3107.4166 | 245 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5697 | 422 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 553.9545 | 56.43 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1400 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 49.0833 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 57 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 291.9 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 150.423 | 3.42 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 378 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5816.6666 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 480.85 | 59 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 287 | 82 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5287.6998 | 363 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1384 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1807.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 477.25 | 57.5 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 340 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26.8333 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.05 | 81 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.75 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 198.85 | 41 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 228.6665 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 299.8333 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 336 | 67.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 575.1666 | 119 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 996 | 240 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1223.75 | 445 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1420.8332 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2167.5 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.4 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61.5 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142.5 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171.5 | 98 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 457.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 979.1665 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12037.9999 | 312 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 19.464 | 48.66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41.6666 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 188.9333 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 540 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1728.6 | 258 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 402.1333 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 475.6 | 12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 35.85 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 119.6 | 12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 37.675 | 16.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 306 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 75.3667 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326.6665 | 175 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1629.875 | 110.5 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2591.6665 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102.265 | 18.1 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 435 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11484 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.6666 | 125 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44 | 44 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.6666 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 236.6667 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 247.9997 | 480 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 568.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 571.32 | 47.61 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2832.2999 | 162 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3185.9999 | 324 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5780.6666 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49.5 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 54.0949 | 104.7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163 | 32.6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1025.7331 | 314 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1114.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1153.75 | 355 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1485 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3183.3333 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.2 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 29.196 | 48.66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 81 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 175 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 178.5 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 223.98 | 37.33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 307.2832 | 179 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 477.6333 | 178 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 509.6666 | 278 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 691.1665 | 319 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 751.3333 | 56 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 893.3332 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1046.5 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1335.4666 | 128 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1562.3332 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 456.413 | 147.23 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2433.3333 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13300 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13377 | 343 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 218.5 | 23 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 253 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 80.6 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 69.6667 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 157.29 | 52.43 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 85.85 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 92.65 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.5667 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 70.8333 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 174.9999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 562 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 862.3999 | 231 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 947.5999 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1805.6 | 488 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.5 | 3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.4167 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35 | 17.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 71.25 | 95 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266.6666 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 299.25 | 66.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 430 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 631.8666 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 927.5 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.6667 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.5 | 2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.6833 | 33.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.875 | 31.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 127.0833 | 125 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 165.6666 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 202.5 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 228 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 432 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 624 | 520 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 824.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 908.6666 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1179.9999 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 50.25 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 88.0333 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 169.3113 | 2.92 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 453.4833 | 91 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1770 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1521.9 | 178 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9339.5832 | 125 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23197.7999 | 414 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 139.4 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39 | 39 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80.75 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.2666 | 109 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.8333 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 191.4 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 395.25 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 572.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 580.1332 | 152 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1146.25 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1359.5832 | 251 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1479.3999 | 156 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3049.7499 | 165 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.6667 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.3333 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 358.75 | 205 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440.6667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1147.5 | 255 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148.2833 | 41 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.7 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252.4 | 63.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 291.8332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 355 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1090 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1737.6666 | 260 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2504.9997 | 450 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2697.03 | 299.67 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3087 | 245 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 700 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 461.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 506.24 | 4.48 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.1667 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1615 | 190 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 166.9186 | 54.43 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 283.5 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 700.4 | 206 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2966.05 | 433 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2800 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.3333 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 87.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 916.6665 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55612.083 | 575 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.8666 | 134 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 71.25 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 99.99 | 33.33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132 | 44 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287.5 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 311.6 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 356.3333 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 564 | 141 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 591.5832 | 155 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 686.25 | 183 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 847.1666 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1144.7999 | 324 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1201.6665 | 175 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2379.6999 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4240 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4619.6999 | 162 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.4167 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.3333 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 202.5 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 321.75 | 117 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 322.5 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 585 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 714.3999 | 141 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1112.0833 | 157 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1122.9166 | 245 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1430.1832 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2208.3332 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11939.5332 | 316 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.9167 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.88 | 82.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.5 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.8333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104 | 32 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240.25 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 431.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 845.25 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1133.3332 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2208.75 | 475 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3328.5 | 210 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5915 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 34 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 51.9333 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 295.1333 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1877.3331 | 640 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2025 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1165.5833 | 71 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 848 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 149.8566 | 67.1 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2543.297 | 466.66 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11779.583 | 425 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 515.9833 | 83 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7559.3331 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63778.3996 | 588 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 147.3332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.5831 | 275 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.4166 | 155 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290.3333 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 304.2 | 468 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 441.75 | 19 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 810 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1563.3 | 81 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2772 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3475 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4077.3999 | 174 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6509.9999 | 360 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.4667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 262.5 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 314.25 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 362.2666 | 104 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 387.7163 | 541 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 413.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 427.5 | 285 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2138.5 | 235 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2420 | 275 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2742.6666 | 55 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 154.9333 | 166 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 771.875 | 32.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1666.75 | 295 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7065 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 19.6667 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 238.7 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 9.8166 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 58.3833 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 29.1333 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1170 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3580.7271 | 315.02 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3118.7333 | 163 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.326 | 101.34 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1810.9 | 199 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 274.0833 | 57.5 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55805.6663 | 580 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 157 | 31.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 45.6 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 204.23 | 15.71 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 300.96 | 12.54 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 247.5333 | 79 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 15.2 | 15.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 51.88 | 25.94 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1229.9999 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 560 | 32 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 25.53 | 25.53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 128.1583 | 3.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1635.1165 | 199 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 11.75 | 11.75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 32.48 | 16.24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 27.5 | 37.5 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 37.2 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Other | BM | 800 | Miscellaneous | WECC | Summer | 14.6183 | 17.9 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 64.05 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 94.25 | 29 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 22.9667 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 94.15 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 102.6666 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 5.7333 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 33.9 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 114.0666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 205.3333 | 88 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 330.3999 | 168 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 396.3333 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1250.6665 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 12.4166 | 149 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 46.1999 | 198 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 768.1665 | 419 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 338 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 547.1664 | 469 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 8044.2 | 369 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 26.8 | 134 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2514.6665 | 368 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 290.6666 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 69.1667 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 798.25 | 103 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 62.3333 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 207.6 | 519 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 254.3332 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 261.6 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 344.4999 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 645.75 | 369 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1209.9 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 9913.7998 | 369 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 185.9 | 169 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1763.1998 | 348 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5328 | 288 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 212.5 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 11.3333 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 188.4999 | 78 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 369.5999 | 198 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 904.6666 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 127.8333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 577.6998 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1384.6665 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 34.5 | 69 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 349.7 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 9 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 39.3333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 52.9998 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 98.9 | 69 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 133.5 | 89 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 627.25 | 193 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 949.7331 | 419 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1744 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 38.8333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 24.5833 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5554.5 | 210 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 49.1666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 82.6 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 539.4999 | 78 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 114.4666 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 368.6666 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 11.3333 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 173.8332 | 298 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 739.75 | 269 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 329.55 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 170.7999 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 921.1999 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 4443.8331 | 293 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 64 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 80.6333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2860.7999 | 288 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 143 | 143 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 170.2 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 182.25 | 243 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 184.8666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 711.75 | 219 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1199 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2107.1666 | 269 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 100.45 | 49 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 945.9832 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3823.2997 | 519 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 164.3333 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1923.9498 | 483 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 6000.1665 | 518 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 69.5166 | 43 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 139.6333 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 275.3333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 31.8 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 635.7332 | 298 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 113.85 | 69 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 142.35 | 219 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 168.8666 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 577.7 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 938 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 585 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 920 | 92 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 179.0666 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 149.3332 | 128 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 420 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 24.75 | 99 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1449.9999 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1901.3331 | 368 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 358.6666 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 212.5 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 51.1333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 279.9999 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 21 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 42.25 | 39 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1518.2666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 69.0333 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 756 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1770.2499 | 219 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1887.0499 | 219 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 25.4333 | 109 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 90.4666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2495.4997 | 483 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 163.0833 | 95 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 60 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 780 | 60 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 492 | 45 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 220 | 120 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 374.5832 | 155 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 279.3331 | 419 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 22835.5 | 419 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 48703.3331 | 769 | 1 | 1 | 0050-Coal storage fires | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 342.1831 | 419 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1465.2 | 444 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 7702.6165 | 419 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 41244.0331 | 769 | 1 | 1 | 0050-Coal storage fires | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1354.2 | 444 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.1666 | 58 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.0833 | 59 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187.3333 | 4 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 499.4667 | 16 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 360 | 96 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26 | 12 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 54.6 | 4 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 70.05 | 9 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 256 | 16 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 574 | 14 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1740 | 174 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 244.8 | 204 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 114.4 | 52.8 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.1666 | 58 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.5333 | 68 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20104.5 | 65 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.4166 | 59 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122 | 61 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.6666 | 76 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 509.1667 | 5 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9780 | 30 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 123.25 | 85 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124 | 62 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326.6666 | 200 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7264.5 | 174 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.8333 | 58 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1333.1667 | 19 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4117.5 | 135 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 775.5 | 94 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1360 | 80 | 2 | 2 | 0060-Coal crushers including motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.8333 | 10 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 339.25 | 23 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 203 | 20 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 630 | 45 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.15 | 81 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 50.1166 | 31 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 163.9999 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 165 | 15 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 238 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 174.1667 | 10 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1.95 | 7.8 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4339.3333 | 40 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3.6666 | 55 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 347.2 | 124 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1298.4999 | 318 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3611.6665 | 220 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 112.5 | 125 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 419.3333 | 74 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.1333 | 71 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92.6666 | 139 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 160 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 178 | 178 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 365.3 | 281 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 258 | 40 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.9 | 33 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 10 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 76.2499 | 183 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1881.3333 | 80 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.8333 | 3.8 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60.5 | 30 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187.5332 | 194 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 237 | 237 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 12.1833 | 43 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.4666 | 74 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 175.5 | 13 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 446.8333 | 7 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 16.7333 | 4 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 54.0583 | 6.5 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 56.1 | 18 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 10.4 | 4 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 137.25 | 549 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 385.9996 | 579 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 497.1497 | 489 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1295.8 | 589 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 48.5333 | 28 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 82.5 | 30 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 17.25 | 23 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 362.1 | 51 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 60 | 20 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 93.1 | 38 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 240.7 | 58 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 28.9333 | 28 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 74.4333 | 58 | 1 | 2 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 6.65 | 19 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 54.4667 | 38 | 1 | 1 | 0080-Stackers/reclaimers | D2-Forced - Delayed | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 362.95 | 51 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 21 | 21 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 219.8 | 21 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 7.5 | 10 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 565.4166 | 115 | 1 | 1 | 0080-Stackers/reclaimers | D2-Forced - Delayed | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 43.0667 | 38 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 48.6 | 54 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 174.1166 | 31 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 113.3333 | 25 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 18.3333 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 3.2667 | 7 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 41.1667 | 26 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 94.0333 | 26 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 103.1333 | 26 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 34.85 | 17 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 228.6333 | 38 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 10 | 10 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 15.54 | 15.54 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1228.5 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 313.8333 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D2-Forced - Delayed | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 4680 | 50 | 1 | 1 | 0080-Stackers/reclaimers | U2-Forced - Delayed | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1818.3333 | 50 | 1 | 1 | 0080-Stackers/reclaimers | U2-Forced - Delayed | 650-Fluidized Bed
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 798.3333 | 100 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 30.1 | 43 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 60.8333 | 50 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | U1-Forced - Immediate | 650-Fluidized Bed
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1024.98 | 93.18 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 20.7133 | 47.8 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210 | 120 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.75 | 95 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64.1667 | 22 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2768.8164 | 713 | 1 | 1 | 0085-Bunker feeder coal scales | U1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 13.3 | 39.9 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 89.8333 | 22 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 146.6667 | 32 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 650-Fluidized Bed
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 207.99 | 69.33 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1615 | 190 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.8 | 34 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 15 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278.0833 | 47 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3730 | 120 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 267 | 89 | 1 | 1 | 0090-Bunker fires | D2-Forced - Delayed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.25 | 21 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.45 | 19 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1666.6666 | 100 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.5833 | 35 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 202.6666 | 160 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 338.0806 | 100.42 | 1 | 1 | 0090-Bunker fires | D3-Forced - Postponed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 557.35 | 157 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.25 | 17 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 806.6667 | 22 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 182.55 | 9 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 45.5 | 13 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 800-Miscellaneous
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 672.6667 | 20 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.7833 | 31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85 | 42.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 229.5 | 54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.5 | 31.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 712.5 | 125 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 28.3333 | 20 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 295 | 60 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 613.5833 | 199 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2209.9999 | 150 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 945 | 63 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 490.2 | 11.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 226.2 | 36 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 37.9833 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 50 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60 | 72 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.8 | 44 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 684.6666 | 104 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 916.6666 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1835.8333 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1608 | 120 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2.8 | 14 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.7999 | 96 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.3333 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2174.3333 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 321.6 | 13.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 171.6667 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 278.6667 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 64.5433 | 3.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 29.4 | 9.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 173.2108 | 17.35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.3333 | 2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.9117 | 5.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.6 | 76 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216 | 120 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6979 | 60 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.5833 | 13 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.6667 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.1833 | 83 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.3333 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.6667 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 416.25 | 45 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2867.6999 | 99 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4753.3333 | 184 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 475.6 | 16.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 75.0833 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 95.4 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 18 | 6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 700 | 140 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 682.4999 | 225 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.7658 | 18.05 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.05 | 23 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.4 | 56 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.75 | 195 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.375 | 7.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.0283 | 10.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 258.7167 | 1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 289.6 | 48 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 689.1667 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 801.7833 | 73 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1050.5 | 382 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.1 | 6.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1128.3333 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2146.2499 | 75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2051.24 | 11.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 22.1 | 1.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 11.8 | 12 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 739.1667 | 50 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 419.0833 | 235 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2104.8499 | 129 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.5033 | 5.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.9167 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.0833 | 65 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.986 | 9.96 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.3333 | 178 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 235 | 235 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 545.4166 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 767.0305 | 198.37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.7383 | 2.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.66 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225.8666 | 176 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 607.4283 | 28.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1956.9999 | 228 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.6666 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.5 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 406.6666 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 31 | 31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 408 | 17 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 16 | 8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.1666 | 28.75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 31.4405 | 48.37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 195.5 | 15 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 338.5433 | 15.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4177.3667 | 14 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39 | 9.75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.6 | 71 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 166.25 | 75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4.6 | 12 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 8.225 | 32.9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.6 | 104 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 451.2 | 9.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 36 | 6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 15 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 24.5 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220 | 110 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1351.4832 | 131 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35629.9998 | 600 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30336 | 158 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.1875 | 28.75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.9083 | 5.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.5832 | 215 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.6217 | 4.7 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.0833 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134.64 | 26.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 309.8333 | 169 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.1667 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 837.5 | 75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 213.3833 | 31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 116.6 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 140.4666 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 763.75 | 47 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.2283 | 4.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.1667 | 10 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.7708 | 28.75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.96 | 17.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.3332 | 224 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.6 | 44 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 140 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474.5666 | 46 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198.3333 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 366.7999 | 84 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1303.6166 | 107 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1953.2 | 11.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 19.8 | 33 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1947.9166 | 85 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | MRO | Summer | 584 | 14.6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | MRO | Summer | 508.8 | 10.6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 96.25 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 9.1 | 7 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | MRO | Summer | 2721.6 | 12.6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | MRO | Summer | 412.8 | 8.6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 320.6 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 848.35 | 19 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 119.5833 | 41 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 83.8666 | 68 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 286 | 20 | 1 | 1 | 0100-Bunker gates | D2-Forced - Delayed | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.7318 | 31.39 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 15 | 1 | 1 | 0100-Bunker gates | D2-Forced - Delayed | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.8667 | 44 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 910 | 280 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.35 | 81 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255.5666 | 82 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 864 | 45 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1895.25 | 35 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1498.75 | 25 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 724.7333 | 14 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125.8333 | 50 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 784 | 28 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 5.6667 | 20 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 32.3 | 38 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 850.75 | 83 | 1 | 1 | 0107-Screen (prior to bunkers) | U1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 10.6 | 53 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 388.7166 | 83 | 1 | 1 | 0107-Screen (prior to bunkers) | U1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 4.05 | 9 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1337.5 | 50 | 1 | 1 | 0107-Screen (prior to bunkers) | U1-Forced - Immediate | 650-Fluidized Bed
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.75 | 45 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48 | 48 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.8 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.6667 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2120.0833 | 95 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2272 | 320 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3036.45 | 653 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.0667 | 8 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 77.5832 | 245 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 93.6 | 78 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 702 | 270 | 2 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 780 | 32.5 | 2 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1542.87 | 49.77 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2372 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4158 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4782.0999 | 174 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5374.9998 | 300 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318.9998 | 660 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.6 | 54 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2662 | 242 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 876.8 | 48 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8370 | 200 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 35.3333 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 362.25 | 9 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2218 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.2 | 42 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.4666 | 28 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.15 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1183.7 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.2 | 83 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.9166 | 31 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.9 | 18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180 | 7.5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 810 | 180 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1367.9998 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1507.4999 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2607.4999 | 75 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 166 | 166 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7076 | 244 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.5 | 63 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 336.895 | 21.9 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.2 | 42 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.7 | 42 | 1 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.2 | 42 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.7 | 42 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 222.9167 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 250.6 | 42 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 356.6998 | 261 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 382.5 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3905 | 284 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30.3333 | 26 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.5833 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.0833 | 125 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 133.02 | 22.17 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 133.7333 | 34 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 138.7667 | 23 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 155 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 320 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 516.25 | 295 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 708.3333 | 125 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 759.5 | 245 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1399.5666 | 242 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1424.3665 | 247 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2052 | 108 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3135 | 209 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.0666 | 28 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 317.05 | 51 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.2 | 32 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92.4666 | 73 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 2 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 451.6667 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.05 | 9 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.2995 | 10.59 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 344.1 | 74 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3758.1332 | 272 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3771.9498 | 273 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.7 | 66 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 495 | 99 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 931.6 | 51 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 28.6667 | 8 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.85 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 344.0799 | 224.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.8 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.6 | 21 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195.0666 | 152 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 258.6666 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1030.6667 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1508.75 | 85 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2127.5 | 230 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102.4999 | 150 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121.25 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186.2333 | 74 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 293.25 | 85 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 620 | 310 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 764.9999 | 135 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1440.8333 | 247 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.2 | 86 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 614.4 | 256 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 683.3332 | 200 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 915.1332 | 259 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 407.9331 | 422 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.8 | 28 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.4 | 42 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107.1 | 42 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 267.9075 | 119.07 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 346.5 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 429 | 195 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 577.6 | 152 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2225.7497 | 435 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3080 | 440 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3161.8666 | 284 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.1667 | 38 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 88.5 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266.5 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 283.5 | 54 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 632.5 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2344.4999 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7520.3328 | 770 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13300.1 | 113 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.9 | 21 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66.5 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66.6666 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1581.75 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.9167 | 35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 750 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3136.4165 | 617 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.3333 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72 | 32 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 457.275 | 87.1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1435.8998 | 249 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.9286 | 75.16 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85 | 34 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 799.0166 | 251 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 918.4999 | 330 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.2 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37 | 6 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.5 | 30 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329.5833 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 546 | 63 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 725 | 290 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 910 | 130 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1088 | 128 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.8333 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.6649 | 172.35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.25 | 125 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.75 | 33 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161.6666 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 654.7333 | 2 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 801.4165 | 295 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1877.3331 | 320 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1205 | 241 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1393.4166 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117 | 260 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | SF-Startup Failure | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19275.6664 | 770 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 231.0166 | 83 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 650-Fluidized Bed
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1.8 | 3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 800-Miscellaneous
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 125.6667 | 13 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 800-Miscellaneous
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1183.9997 | 444 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 558.6665 | 419 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 344.4999 | 318 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 19 | 9.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 304 | 30.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 289.85 | 33 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 661.9917 | 11.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Winter | 103.8916 | 68.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 483.3333 | 50 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 23.2 | 8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 23.82 | 11.91 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 101.55 | 6.77 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 106.3333 | 72.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 2331.82 | 37.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 224.1066 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 83.9583 | 12.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 6.72 | 6.72 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 30.28 | 7.57 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 10 | 50 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 25.375 | 10.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 87.4 | 38 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 4.4 | 2.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 9.51 | 9.51 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 392.755 | 9.65 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 2223 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 3161.6667 | 50 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 2445.8333 | 50 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 975.96 | 108.44 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 118.86 | 5.66 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 96.875 | 62.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 125.4166 | 87.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 70.8333 | 50 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 43.5 | 14.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 34.77 | 12.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 11.7583 | 41.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 34.32 | 5.72 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 314.1 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 45.628 | 11.22 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 390.96 | 48.87 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 1012.15 | 32.65 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 2323.5 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 261.03 | 37.29 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 39.375 | 12.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1321.92 | 73.44 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 2.05 | 2.05 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 6.15 | 2.05 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | BM | 800 | Miscellaneous | SERC | Winter | 181.5 | 66 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 800 | Miscellaneous | WECC | Winter | 162.76 | 15.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 800 | Miscellaneous | WECC | Winter | 405.5833 | 15.7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 75.9 | 13.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 90.85 | 15.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 800 | Miscellaneous | WECC | Winter | 277.2467 | 18.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 10.2916 | 47.5 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 89.6 | 12.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 136.5 | 19.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12.3 | 4.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 144.4 | 3.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 10.2 | 3.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 41.6 | 5.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 15.2 | 7.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 17.2 | 4.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 163.4 | 3.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 18.2 | 9.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 32 | 4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 42.9 | 14.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 75 | 15 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 196.2 | 21.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 10 | 10 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 29.6 | 7.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 21.63 | 21.63 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 5.2 | 5.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 156.8 | 9.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 0 | 0 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | NPCC | Summer | 731.875 | 37.5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | U1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 88 | 120 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | NPCC | Summer | 73.6965 | 27.81 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 116.51 | 12.2 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 110.0033 | 12.2 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 37.5 | 12.5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Winter | 45.0416 | 57.5 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 675 | 50 | 1 | 1 | 0116-Solid fuel feeder motors | U1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 454.4167 | 35 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 875.8333 | 25 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 280.9333 | 49 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 800-Miscellaneous
0119 | Solid fuel crushers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 46.125 | 7.5 | 1 | 1 | 0119-Solid fuel crushers | D1-Forced - Immediate | 650-Fluidized Bed
0119 | Solid fuel crushers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 22.5 | 7.5 | 1 | 1 | 0119-Solid fuel crushers | D1-Forced - Immediate | 650-Fluidized Bed
0119 | Solid fuel crushers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 422.03 | 60.29 | 1 | 1 | 0119-Solid fuel crushers | D1-Forced - Immediate | 650-Fluidized Bed
0119 | Solid fuel crushers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 53.75 | 7.5 | 1 | 1 | 0119-Solid fuel crushers | D1-Forced - Immediate | 650-Fluidized Bed
0119 | Solid fuel crushers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 5.2267 | 5.6 | 1 | 1 | 0119-Solid fuel crushers | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 2.1567 | 0.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 4.5442 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 18.45 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 154 | 30.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 1278.56 | 104.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.005 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.38867 | 0.53 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.081 | 0.69 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.8685 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 8.3098 | 6.83 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 0.59167 | 0.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.3427 | 0.53 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.5823 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.9022 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.9358 | 1.01 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 2.05 | 2.05 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 10.206 | 1.26 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 20.05 | 3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 1.025 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 1.4833 | 0.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 7.8583 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 28.0167 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 9 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 648 | 64.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | NPCC | Summer | 5.192 | 5.28 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 1158.4766 | 75.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.018333 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.0225 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.21883 | 1.01 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.37033 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.58917 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.0488 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.9923 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 18.05 | 3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 28.1375 | 22.51 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 2.9948 | 1.51 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 14.35 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.6665 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.919 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 18.4 | 1.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 21.2667 | 2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 0.083333 | 0.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 4.2367 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 16.7417 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 20.175 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 8.925 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 150.99 | 50.33 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 345 | 86.25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 586.1866 | 75.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.008333 | 0.05 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.024167 | 0.05 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.0425 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.097166 | 0.53 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.10667 | 0.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.1615 | 0.51 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.18933 | 0.71 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.255 | 1.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.34317 | 0.71 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.96283 | 0.53 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.292 | 1.52 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 2.05 | 2.05 | 1 | 11 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.717 | 1.26 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 6.04 | 1.51 | 1 | 3 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 12.8333 | 2.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2.448 | 3.06 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 4.843 | 1.67 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 325.972 | 9.08 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 430.8333 | 50 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 1.6333 | 0.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 35.75 | 6.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2.25 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 705.96 | 39.22 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 3272.94 | 118.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.004167 | 0.05 | 1 | 3 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.005833 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.01 | 0.05 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.084166 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.12 | 0.48 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.301 | 0.86 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.62283 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 38.2185 | 5.13 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 2.2 | 2.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 8.2 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 0.58917 | 0.35 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 3.0788 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 6.084 | 1.69 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 6.231 | 2.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 26.368 | 8.24 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 30.3832 | 4.81 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 143.1 | 54 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 1.0933 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 9.225 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 20.125 | 3.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 38.7792 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 71.2375 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.000667 | 0.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.079167 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.475 | 1.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.86917 | 0.35 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.0423 | 0.53 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.4403 | 1.73 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 8.875 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 1.1 | 2.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 1.51 | 1.51 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 0.75517 | 1.97 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 0.87967 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2.5913 | 2.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 14.9148 | 1.09 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 25.432 | 8.67 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 62.0238 | 5.63 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 392.5 | 50 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 9 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 15.1017 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 57.7417 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 94.6758 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 623.04 | 51.92 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 0 | 0 | 1 | 3 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.004 | 0.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.010833 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.0325 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.135 | 0.54 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.142 | 3.06 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.5415 | 2.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.819 | 4.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.4587 | 1.76 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 5.963 | 2.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 8.099 | 5.34 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 34.751 | 17.67 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 4.1 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.2625 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 3.7788 | 0.79 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 4.1 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 213.3863 | 2.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 283.9807 | 3.64 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 27.0833 | 25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 0.5125 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 2.3233 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 5.125 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 153.5667 | 17 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 31.8333 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 51 | 25.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 26.68 | 13.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.007 | 0.06 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.024666 | 0.74 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.063 | 0.18 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.063 | 0.42 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.52 | 2.08 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.52183 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.82483 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.0725 | 0.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.5823 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.6378 | 2.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 4.53 | 1.51 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 7.55 | 1.51 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 14.833 | 3.26 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 24.4407 | 12.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 63.55 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 109.0766 | 76.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 200.7 | 54 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 80.1 | 54 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 2.9042 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 23.37 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 59.5 | 3.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 108.3767 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 219 | 14.6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.003333 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.028333 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.0555 | 0.37 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.16833 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.23567 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.3535 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.78617 | 0.53 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.84167 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.1447 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 6.4225 | 3.67 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 48.048 | 2.88 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 2.05 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 0.063333 | 0.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 0.188 | 0.94 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2.508 | 1.52 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 6.925 | 1.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 25.7767 | 1.85 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 302.94 | 5.61 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 220.72 | 37.2 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 244.8 | 54 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | BM | 800 | Miscellaneous | WECC | Winter | 128 | 16 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 888.7916 | 128.5 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 750 | 125 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 53.625 | 6.5 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 650-Fluidized Bed
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.5 | 15 | 1 | 1 | 0126-Coal crusher lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88.6125 | 38.25 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 416.6666 | 40 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1792.4166 | 157 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.3333 | 76 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.9999 | 120 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 457.9166 | 157 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.875 | 62.5 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D2-Forced - Delayed | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.4166 | 157 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 370 | 148 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 296.875 | 62.5 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 188.49 | 125.66 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 738.6666 | 138.5 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 3 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 169 | 13 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 357.9333 | 52 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 727.9999 | 240 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 884.5333 | 124 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6995.8333 | 115 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 1 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 405.8333 | 25 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1466.4999 | 210 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 27 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 66.75 | 89 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 552 | 460 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1229.7333 | 23 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.9833 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 911.625 | 66.3 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.9 | 6 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1055.97 | 117.33 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110 | 44 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 91 | 14 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 260.9999 | 108 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 378 | 189 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 440.5333 | 64 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7062.5 | 113 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1693.98 | 188.22 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1632 | 320 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.4667 | 22 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1892.1466 | 167.2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 4.3333 | 13 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.4999 | 93 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 466.2333 | 71 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2365 | 215 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135.25 | 54.1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 888.25 | 209 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.66 | 5.11 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56 | 21 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.8833 | 7 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 440.75 | 43 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 723.9998 | 240 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 231.99 | 77.33 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 50 | 50 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 17 | 51 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | RFC | Off-Peak | 82 | 41 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 121.99 | 11.09 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0134 | Sorbent handling crushers | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 34.1413 | 18.29 | 1 | 1 | 0134-Sorbent handling crushers | D1-Forced - Immediate | 650-Fluidized Bed
0134 | Sorbent handling crushers | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 40 | 20 | 1 | 1 | 0134-Sorbent handling crushers | D1-Forced - Immediate | 650-Fluidized Bed
0152 | Sorbent feed volumetric feeder | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 375 | 75 | 1 | 1 | 0152-Sorbent feed volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0152 | Sorbent feed volumetric feeder | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 476.4833 | 113 | 1 | 1 | 0152-Sorbent feed volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0152 | Sorbent feed volumetric feeder | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 952.9333 | 56 | 1 | 1 | 0152-Sorbent feed volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0152 | Sorbent feed volumetric feeder | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 32.8166 | 35.8 | 1 | 1 | 0152-Sorbent feed volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0152 | Sorbent feed volumetric feeder | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 183.3167 | 17 | 1 | 1 | 0152-Sorbent feed volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0155 | Sorbent feed pneumatic transport system including piping and valves | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 396.5 | 39 | 1 | 1 | 0155-Sorbent feed pneumatic transport system including piping and valves | D1-Forced - Immediate | 650-Fluidized Bed
0155 | Sorbent feed pneumatic transport system including piping and valves | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 84 | 42 | 1 | 1 | 0155-Sorbent feed pneumatic transport system including piping and valves | D1-Forced - Immediate | 650-Fluidized Bed
0160 | Bed material tanks/hoppers | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 11196.5333 | 35.2 | 1 | 1 | 0160-Bed material tanks/hoppers | U1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 366.2666 | 67 | 1 | 1 | 0163-Bed material feeders | U1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 0.96667 | 2 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 132.8586 | 34.36 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 1341.8666 | 125.8 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 1321.84 | 37.2 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 650-Fluidized Bed
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.5832 | 131 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 125 | 125 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 420 | 70 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 647 | 60 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 313.3 | 39 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4476.9666 | 49 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.0333 | 11 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 623.7 | 154 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59899.9999 | 75 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2681.7999 | 318 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | U2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3953.6 | 56 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2558.5 | 119 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.5 | 17 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 219.95 | 53 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5276.3333 | 110 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 139 | 139 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190.6666 | 52 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1273.5999 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1616 | 202 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131 | 131 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105 | 105 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21.1666 | 127 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110.1999 | 114 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155 | 155 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105.6 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.9166 | 127 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.3333 | 65 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1997.25 | 45 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.5 | 30 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2269.2 | 488 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 851.285 | 19.13 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2767.5 | 30 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 283.6666 | 74 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 389.5 | 95 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.9 | 38 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1429.1666 | 70 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 21685.2999 | 78 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 484.8999 | 78 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4959.5 | 78 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 143.65 | 17 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 568.3333 | 110 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 570 | 30 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 923.75 | 75 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 926.8333 | 10 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 285 | 95 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.3333 | 14 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.0833 | 53 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3375.9 | 54 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2717.0666 | 46 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2231.5333 | 44 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 80 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 30 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 253.1667 | 35 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2280 | 25 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9825 | 150 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1200.9833 | 23 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 793.3333 | 80 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6998.3333 | 85 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19 | 38 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 26.3333 | 39.5 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168.75 | 75 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3214 | 60 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 671.8333 | 139 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3560.7 | 78 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105 | 10 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180.5 | 30 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 515.2 | 64.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.4 | 14 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8938 | 872 | 1 | 1 | 0205-Pulverizer exhauster fan drive | U1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 35 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3348 | 124 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 585.3333 | 40 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 921.6 | 36 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 217.5999 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 276 | 23 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1062 | 54 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 22278.6664 | 385 | 1 | 1 | 0205-Pulverizer exhauster fan drive | U1-Forced - Immediate | 100-Fossil-Steam
0210 | Pulverizer heater (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 141.75 | 81 | 1 | 1 | 0210-Pulverizer heater (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0220 | Pulverizer system cyclone separator | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107.7 | 18 | 1 | 1 | 0220-Pulverizer system cyclone separator | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.4166 | 95 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.6 | 78 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132 | 66 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136 | 68 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 346.5 | 33 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 370 | 20 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 635.25 | 33 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 822.3999 | 96 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1757.7 | 54 | 1 | 1 | 0240-Pulverized coal bin | U1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 311.9999 | 144 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 404.7 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 663 | 170 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.3 | 83 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.65 | 37 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40 | 200 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71 | 71 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 117.5999 | 144 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 516 | 129 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.4 | 48 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68 | 68 | 1 | 2 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 102.688 | 32.09 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3764.8 | 104 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 281 | 70.25 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.5 | 129 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 335.25 | 149 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1375 | 275 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66 | 66 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67 | 67 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100 | 30 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142 | 71 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166.6666 | 80 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 249.0833 | 61 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 360 | 144 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 215 | 150 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72 | 72 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.6 | 78 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.8733 | 30.8 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 123.75 | 99 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.4 | 94 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52 | 26 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64 | 64 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122 | 61 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.3333 | 65 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 171 | 76 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210 | 70 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 368.1666 | 94 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.5999 | 78 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 505 | 101 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.4533 | 14.8 | 1 | 1 | 0240-Pulverized coal bin | D2-Forced - Delayed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 184.1666 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 197.9498 | 321 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.6 | 28.8 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.5999 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 10 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 292.5 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121.25 | 97 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5229.76 | 88.64 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 202.9999 | 174 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 572 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.2 | 31.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.6 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.6333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.6666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 14.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.1333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.4666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.2 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.5033 | 64.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 24.984 | 62.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.0667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.0333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.5 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.0833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.6666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.4833 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.5667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.8667 | 41.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59 | 295 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60 | 30 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.2667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.5 | 37.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.5333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.6666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88.6667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.9999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.8012 | 125.54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.8666 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 133.3332 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160.9999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 172 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 174.5333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 178.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 180.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 194.75 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 206.25 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 250.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 297.6665 | 235 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 309.7333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 371.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 373.1 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 386.3333 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 398.9333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 426.3 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437.5 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 534 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 543.7499 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 546.9333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 706.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 756.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 767.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 829.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 843.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 863.2666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1038 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1068.75 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2461.25 | 179 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3528.8999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4298.4 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10496 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1.35 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.1333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.9333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.5 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.75 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.8333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.02 | 25.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3333 | 100 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 15.432 | 38.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.7999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.0833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.9333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.205 | 84.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.4 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.65 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.3833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.4333 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 100 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.3333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.7333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.75 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75.0667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.3333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.5 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94.2 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115.5 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115.7333 | 217 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 133.9333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 136.1666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 144 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173.4066 | 136.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 176 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 194.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.75 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 199.5 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 208.6665 | 313 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 239.7332 | 248 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 251.8833 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 252 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 273.0666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 279.8166 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 313.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 333.3666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 356.4 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 383.4 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 383.8333 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 403.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 419.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 431.5999 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 433.5833 | 236.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 436.5 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 441 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 475.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 541.4999 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 574.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 606.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 687.1665 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 695 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 770.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 784 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 922.1333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1356 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1883.3332 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3291.6665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4025.2499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.3 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.2667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 8.8843 | 48.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.8166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.6666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.895 | 33.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.9566 | 64.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.4 | 30.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.8333 | 62.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.4 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.786 | 50.97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.6666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.0253 | 9.94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.2667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 57 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.7333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 71.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 75.3999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 81.545 | 104.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 83.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.2 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.8 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.6316 | 156.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97.1666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 112.05 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 122.2666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.9 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 128 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 151.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 153.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156.25 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162.6666 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 212.5 | 12.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 214.5 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220.4 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 240 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 245.25 | 54.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 262.77 | 175.18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 288 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 323 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 337.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 385 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 418 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 427.2666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 550 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 733.8999 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1059.1666 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1096 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1179.3333 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1868.2666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2235.7332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3060.75 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4821.2499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.4667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.8 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 599.95 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.0833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.95 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 256.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 36.6666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76.6666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 283.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 595.98 | 99.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1050 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.085 | 32.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.7683 | 30.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.98 | 46.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.28 | 43.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.4166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165.64 | 49.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.58 | 27.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.95 | 39 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 560.0467 | 30.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2399.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.9983 | 32.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.1133 | 19.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.84 | 21.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.84 | 56.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 245.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 249.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 314.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 397.3 | 58 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 611.05 | 121 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 751.75 | 97 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 227.1666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 357.2 | 47 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 390.8299 | 125.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 833.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2781.8499 | 177 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70.9166 | 185 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 159.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 370.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 900 | 100 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 632.7 | 111 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 549.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 246.45 | 53 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 650.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3230.0832 | 415 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.8333 | 85 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2342.1663 | 598 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.94996 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.2167 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8583 | 24.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.88 | 2.88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.0333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.055 | 121.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 7.4867 | 22.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.125 | 24.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.9999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.25 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.56 | 62.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.6666 | 100 | 1 | 4 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.59 | 33.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.0366 | 60.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 57.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.95 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.8666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.6666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.1083 | 33.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.9 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.4933 | 31.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.3678 | 44.21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.1802 | 11.11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.7533 | 58.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.575 | 74.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63.3333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.6166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.6666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.7333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.7498 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.9 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.4999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129 | 22.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.1166 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.8665 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184.6332 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 186.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 192 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 231.77 | 47.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 232.1 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 257.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332.9165 | 235 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 345.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 353.0833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 363.8333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 369.185 | 157.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 381.3333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 400.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 424.5666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 444 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 454.4833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 463.975 | 138.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 483.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 512.5333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 588.7999 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 604 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 621.9666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 677.7333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 895.7 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 967.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1094.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1331.1832 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1493.3332 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1560.1666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1719.1333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.99999 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.9366 | 41.62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.35 | 24.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.9333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.1 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.75 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.1833 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.2 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 18.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.46 | 55.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.7866 | 68.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.6666 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.2833 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.75 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.3833 | 33.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.0883 | 31.79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.8333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.355 | 91.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.5 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.75 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.75 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.1667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77.3333 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.4 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.6833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.6666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 130.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132.5333 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 145 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.9 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155.8333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 205.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.1666 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 233.9333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 242.35 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 256 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 267.6 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 288.9999 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 337.7167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 360.7333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 402.0666 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 536.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 571.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 622.8333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 653 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 806.2 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 873.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 917.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1007.4999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1195.7 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1541.3499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2018.4166 | 114.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2035 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2340 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.7067 | 6.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.25 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.4667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.3333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.4 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4.95 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.5 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.1767 | 10.9 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.3333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.4666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15 | 60 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.15 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.4 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.3666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 21.45 | 19.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.3 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26.4 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.0166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.875 | 62.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.2499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.4333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.1333 | 244 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.5158 | 35.05 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.2333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.15 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.6 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.9333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 91.77 | 8.55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 129.0666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.4832 | 228.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 150 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 162 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 166.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.6 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226.4166 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 250.1333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 265 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 286.1666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 299.6666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 318.2 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 326.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 332.9333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 371.3 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 423 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 447.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 488.7 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 580 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 602.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 625.7416 | 63.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 691.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 943.4 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1214.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1332.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1651.8333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2357.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2394.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3153.4998 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5.3167 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66.7 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 157.1666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 299.6 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.4 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70.5 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 473.7005 | 75.39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1796.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5.33 | 31.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 131.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 149.9333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 159 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 868.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.3633 | 23.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.5717 | 21.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.2 | 24 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.065 | 20.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.48 | 22.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255 | 25.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 899.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1449.1665 | 235 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.2867 | 23.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.4383 | 25.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.1817 | 14.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.84 | 27.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.14 | 13.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191.8 | 27.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75.9999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 762.55 | 151 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.1333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 563.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 610 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 870.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 280 | 70 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 19.2 | 48 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.2666 | 86 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1475 | 500 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1984.5 | 135 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.4035 | 3.21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.5 | 35 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.4 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.4016 | 73.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.5167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.8333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.6627 | 35.48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.1666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 46.35 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50.2332 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50.4166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.6 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.625 | 52.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.7 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.9 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.5999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.5833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 109.32 | 54.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.1667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.1667 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120.3666 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.5 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.5 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 143.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147.2166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160.5833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163.2333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 168.9999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 169.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 182.7 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 188.762 | 19.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190 | 47.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 193.3333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204.45 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 205.3333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.7666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 229.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.2666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 261.5833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 268.6 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 295 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 308.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 308.3333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 335.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 341 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 344.75 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 368.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 384 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 474.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 506.25 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 538.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 553.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 554.715 | 105.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 597.52 | 54.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 622.125 | 118.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 637.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 650.8916 | 211.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 661.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 740 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 824.85 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 827.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 889.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1008 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1140 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1140.5333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1514.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4295.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.26 | 22.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.4333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.05 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.1999 | 186 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.3666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.5417 | 27.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.9958 | 50.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.8333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.75 | 55 | 1 | 5 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.3333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.4667 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.25 | 65 | 1 | 6 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.8499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.8333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.65 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.8666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.5 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.834 | 31.16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35.9333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.4333 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.45 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.8 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.3665 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.5333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.5 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.9333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98.8166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.7833 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119.8666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.7333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 127.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 133.1 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 144.5332 | 271 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 161.2 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164.25 | 109.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 191.5833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 231.7333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 236.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.9999 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 250.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 292.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 320 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 327.0833 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 334.8 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 335.7667 | 14 | 1 | 3 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 407.75 | 233 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 467.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 509.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 567.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 677.1 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 681.3331 | 365 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 792.12 | 172.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 843.024 | 92.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 950.0166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1040 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1220.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2883.5666 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.05 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.3333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.68 | 8.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.8666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 6.825 | 19.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.9125 | 19.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.0817 | 18.65 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.5833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.95 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.8667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 16.1 | 34.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.2496 | 31.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32.6166 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.5833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 58.2666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.6533 | 33.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61.1332 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.36 | 22.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.4666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.3166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 76.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 79.1 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 84.05 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 86.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 109.3333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 127.75 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 131.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 136.85 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 142.3333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.04 | 207.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 162.9166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 165.3666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 172.9166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 182 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 194.4 | 243 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 215.2166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235.2 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.6666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 251.7332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 253.5 | 169 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 274.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 306.6666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 312.9 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 427.35 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 430 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 478.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 483 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 505.4333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 552.6333 | 56.2 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 602.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 617.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 688.5 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 720.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 852.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 912.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1052.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1218.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1331.1666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1557.3332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1588.8 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1719.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.7667 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 147.2 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 218.5833 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 320.3333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 348 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 399.96 | 36.36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 548.1 | 109.62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.1 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.45 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 152 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 175.8 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 230 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 585.6246 | 131.11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 81.9 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 464.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 582.55 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 588 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 985.05 | 65.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 114.75 | 4.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.16 | 33.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.6416 | 26.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.4467 | 32.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.165 | 117.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 451.1333 | 67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 800.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.0333 | 13.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 158.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 615.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59.5867 | 21.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.4 | 31.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.05 | 24.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101.1266 | 39.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 277.6666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 589.05 | 119 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.55 | 39 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 200.9 | 98 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 229.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 266 | 133 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 435 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 476.0833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1888 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.1333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.5 | 47 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 143.9999 | 270 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 163.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 201.8332 | 173 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 508.7499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 642.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2296.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 603.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 662.8333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 444.6666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 696.1497 | 459 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.3 | 63 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2043 | 180 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.8333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.9333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.7 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 9.1533 | 27.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 9.6666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.8 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10 | 40 | 1 | 3 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.115 | 28.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.305 | 35.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 12.8333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.8666 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.3333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.825 | 6.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.8 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.8333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.3333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26.3333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.105 | 24.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.3833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.8667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.6499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63.4666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.6665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.5666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.8167 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.9499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109.2 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.5 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144.9 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 147.2166 | 60.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 163.9 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 169.4166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180.25 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 202.6667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.5667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 264 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 267.525 | 61.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 307.0833 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 335.393 | 61.54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.5832 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 369.1999 | 312 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 381.2166 | 257 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 433.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 438.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 499.1999 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 504.5333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 505.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 568.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 586 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 613.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 621.6333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 653.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 666.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 738.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 740.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 792.75 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 819.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 907.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 994.1332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1005 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1037.1666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1038.9332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1075.68 | 43.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1338.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1857.9166 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2062.1999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2776.6666 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3990 | 570 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.3 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.6166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6833 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.8667 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.7167 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.8667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.2 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.1333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.45 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.92 | 31.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.25 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.5 | 50 | 1 | 5 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.2 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 17.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.7656 | 28.39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.1 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.5 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.5 | 17.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.852 | 53.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55.3583 | 94.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.5333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67.5 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97.0666 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.6666 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 104.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105.4499 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.7 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.5 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.1 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.2666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150.65 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164.3 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 168 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177.8666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.6 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 192 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 199.4666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 235 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 260 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 294 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 319 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 345.3333 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 345.4333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 356.4999 | 186 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 377 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 382.0499 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 387 | 129 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 387.9166 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 440 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 462.3331 | 365 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 508.75 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 578.675 | 39.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 589.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 641.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 694.0333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 727 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 779.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 863.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 884 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 910 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 912.9499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 918 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1440 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1503.3666 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1545.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1787.6165 | 283 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3799.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11728.5 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.48 | 2.88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.83333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.93333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.4667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.1667 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.5667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.9333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.2667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.2733 | 45.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.8667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.9166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.9333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.8835 | 48.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.8633 | 72.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26.95 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 29.5533 | 34.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 30.45 | 14.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.55 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 57.4999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.9333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61.8333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.07 | 35.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.6666 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.6 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 77.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 81 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.1333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.7333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.4166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 100.65 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.8 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 130.3332 | 460 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 133.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 158.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 169 | 33.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 178.5 | 59.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196.0666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 232.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 261.2833 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 264.6 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 280 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 319.9833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 326.8 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 352.1833 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 353.3333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 377.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 424.5999 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 432.8 | 54.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 466.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 530.1333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 602.7615 | 99.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 730 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 787.75 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 789.2498 | 231 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 826.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 893.8583 | 48.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 902 | 164 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 963.3332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 981 | 54.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1868.2666 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2108 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4715.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.3 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.9 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 70.9333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.8333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 149.4667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 170.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.7166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 149.5999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 244.4 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 324.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.8 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 535.4833 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.6 | 33 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.21 | 30.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 10 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.555 | 62.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152.4 | 25.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 247.4666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.6 | 23.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.3633 | 35.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.5467 | 20.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.565 | 30.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.3967 | 14.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.875 | 32.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 260 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 442.15 | 71.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 570.8333 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 729.3 | 117 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.6666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 174 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1866.0832 | 245 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 120 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69.3 | 99 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8168.9996 | 630 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1248.3331 | 700 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.52 | 35.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.6 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.8666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.2 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.9333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.7066 | 65.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.1345 | 34.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.5 | 50 | 1 | 3 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.9333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.3333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.8667 | 33.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.6 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23.9167 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.5 | 47.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40 | 100 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.395 | 146.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.85 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.88 | 27.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.4 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.6167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.0166 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.0833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78.4 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.5 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90.3093 | 48.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.65 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.7333 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.35 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 102 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 111 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.6 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 117.1666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 134.9999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.9666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 162.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 184 | 115 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184.15 | 36.83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 186.4333 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 207.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.1114 | 98.19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 271.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 272.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 289.75 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.5833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 324.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 324.9999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 327.6 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 327.7166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 340 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360.8 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 370 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 375.2498 | 285 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 388.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 395.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 406.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 431.2 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 502.045 | 64.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540.8666 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 578.2333 | 166 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 585 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 625.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 654.3999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 661.4666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 668.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 675 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 707.3499 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 781.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 852 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1282 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1451.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1990 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2079 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.15 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.3999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.6667 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.8333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.3333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.9167 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.05 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.5333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.5075 | 86.03 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.3333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.25 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.4 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.0333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.95 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.75 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 59.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.7 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.5 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 92.2666 | 173 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.4 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 113.4 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.0833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 118.8 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 120.3 | 401 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.75 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141.9803 | 27.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170.5 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 171.7333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 208 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 223.25 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 257.5999 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.9 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 265.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 268 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 286.65 | 45.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 298 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 315.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 319.62 | 53.27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 325 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 328.6 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 384.6167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 429.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 431.65 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 450 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 454.1 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 479.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 498.6667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 538.8833 | 217 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 543.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 670 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 739.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 750 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 775 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 819.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 936 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1013 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1041.6666 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1808.6783 | 122.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2187 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5833.8332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.63333 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.25 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3.8875 | 15.55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.1666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.25 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.6667 | 21.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29.5 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.7 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 37.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57.6 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.7333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 66.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.904 | 62.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70.8333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.5667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 76 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.2 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 77.25 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.1 | 110.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100.4667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 102.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 116 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 118.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 120 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 143.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 146.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 147.2166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 159.9 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169.5999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 192.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195.5 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 197.9553 | 65.26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.1666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 219.2833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 219.9166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230.4 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 231.7998 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 239.4 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 243.8333 | 154 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 244.025 | 21.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 252.1666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 266.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280.5333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 354.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 357 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 357.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 414.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 447.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 454 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 511.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 678.6 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 682.5 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 743.6 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 781 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1005.8 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1043.4666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1057.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1931.787 | 90.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4257.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.0333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.502 | 64.17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.0333 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.85 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.0666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.6 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 195.2666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 269.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 946 | 94.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2055 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.1 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 109.65 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 124.1333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 296.725 | 118.69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 621.3013 | 118.72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 153.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.8833 | 24.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.8533 | 55.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.22 | 24.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.48 | 19.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.8333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1742.9165 | 235 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1888.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.2267 | 15.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 620.4833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19278 | 35 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.1067 | 22.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.725 | 31.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.2 | 48 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.4 | 26.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 128.1 | 36.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 724.9999 | 174 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 788.3666 | 134 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.6 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 232 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 372 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2021.6 | 152 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76 | 76 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 313.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 727.3166 | 151 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 847.9 | 122 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1881.3332 | 340 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1430.6999 | 342 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2113.5666 | 163 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.9217 | 20.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.0867 | 33.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.9333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.205 | 47.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.7 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25.6667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.4667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.6667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35.32 | 35.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.5 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.9166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.5 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.7999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 69.789 | 32.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.5 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.5833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 109.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.2499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.9 | 50.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 121 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 140.375 | 22.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.7 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 149.5 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 149.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 156.25 | 125 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 181.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 235.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 253.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 257.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296.1 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 301.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 328.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 331.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 350.6333 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 374.5 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 374.9998 | 450 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 379.9166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 384 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 390 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 459.1666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 485.1666 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 517.3332 | 388 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 527.4858 | 86.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 529.2 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 529.8333 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 544.6667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 616 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 636 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 643.9 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 741.9999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 832.6 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 858.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1213.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1784.6999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4590 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.55 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.7667 | 22.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.125 | 24.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.0833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.8666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.6 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.5333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.4166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.7999 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.75 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.2333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.4 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.5333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.4 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.6666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.65 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.8 | 100.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59.4833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.5 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.8 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.6 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 74 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.8333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.7333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.3166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112.2 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.0166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.5832 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150.4665 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.0332 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180.8333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.1 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 202.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 211 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 227.5 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230.2666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 275 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 303.15 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 335.79 | 172.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 339.9 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 418 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 433.16 | 123.76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 435 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 450 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 509.7592 | 220.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 522 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 588 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 608 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 677.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 753.9999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 773.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1075 | 129 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1098.5333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1521.6666 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3063.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.75 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.5667 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.8333 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.67 | 46.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.8333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.25 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10.9266 | 29.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.775 | 47.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.25 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 25.61 | 59.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.3333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.4333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34 | 40.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 44 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.9833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62.3333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.0666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.8 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 75.9666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101.992 | 40.26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.5 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.0833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 120 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.1 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 136.9165 | 265 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 204.75 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 216.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 231 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 254.0999 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 263.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 313.9333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 327.8 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 335.8333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 348.4433 | 55.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 456.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 471.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 513.3333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 870 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.7333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.4 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.4 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 122.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 148.25 | 148.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160.3333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 191.4 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 303.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 211.168 | 131.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 212.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 222.3953 | 99.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 364.4 | 91.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 62.1 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.65 | 22.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.065 | 25.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.9 | 20.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.2 | 54 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.6 | 52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 522.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 700 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1188 | 108 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 565.4166 | 147.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 934.4999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.78 | 25.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.7133 | 17.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 248 | 12.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 370 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 424.35 | 23 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 439.9999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4608 | 144 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1242 | 270 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.5833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 164.2166 | 167 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41.4 | 138 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 344.25 | 255 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 977.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 291.3331 | 760 | 1 | 1 | 0250-Pulverizer feeders | SF-Startup Failure | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 451.35 | 531 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.5 | 63 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0.58331 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.6 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.875 | 28.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.5333 | 24.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.1833 | 43.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.7833 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.2 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.7783 | 27.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.2666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.1333 | 101.12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 44.061 | 15.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.6666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.9333 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.8999 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.4667 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.75 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 65.105 | 44.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 79.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97.4166 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.05 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 102 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105.3 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.75 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.5 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119.2333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125.25 | 50.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 129.612 | 108.01 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138.8333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 139.15 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 139.5 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 165.1999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 200 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 212.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 235.2991 | 148.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 238.95 | 60.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 253.7 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253.9576 | 119.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290.6667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 301.4666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 301.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 303.3333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 307.0666 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 315.3333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 320 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 351.8666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 355.309 | 82.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 391.6665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 407.7333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 486 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 612.3 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 618.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 681.7 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 687.5 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 714 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 766.8333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 855.508 | 92.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 976 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 978.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1215.0666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1230 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1231.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1233.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3353.4666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5458.3332 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6367 | 22.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.35 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.58 | 28.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.915 | 41.49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.37 | 40.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.8 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.0008 | 54.55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 100 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.5 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.6667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.8666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.4333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.1 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.1333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 31.9833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.1333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.6333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.35 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.5983 | 117.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68.9483 | 100.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.5147 | 24.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.0833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.6816 | 92.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.1333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.25 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130 | 100 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 132 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 141.1666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.5 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.2333 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 146.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 185 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.7 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200.0832 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 201.3833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 224.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 225.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 230 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 233.7 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 255 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 290 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385.6666 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 434.4999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 463.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 500 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 502.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 528.3666 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 529.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 531.6666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 635.8666 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 806.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1150.3333 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1449.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4508.3332 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.5 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.8667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.1 | 49.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.48 | 26.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.5 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.4667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.3 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.6666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.0833 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.4166 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.5 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.9333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.7667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78.2999 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 81.0666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 98.8166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 119 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 124.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 152 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 161.4583 | 62.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164.1166 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 199.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 209.7666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 214.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225.4 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 232 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 243.75 | 325 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 270 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 271.375 | 50.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 339.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 368.1333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 417 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 421.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 515 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 516.6 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 519.0915 | 73.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 554.6666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 567 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 600 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 608.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 711.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 935 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1242.1666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3298.4 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4553.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.1 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 130.2 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 137.2 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.7 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 137.7 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 179.481 | 123.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 109.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 124.2 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 135.1935 | 207.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.7667 | 29.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.385 | 20.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.8 | 22.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.2666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.675 | 16.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158 | 79 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189 | 35 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 451.4999 | 157.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.6216 | 28.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 685.3333 | 128.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.6067 | 24.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.82 | 18.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.41 | 26.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.265 | 33.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124.2133 | 27.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205.6 | 48 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 298.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 331.2833 | 139 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 336.7 | 182 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2288.8666 | 139 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 224.9333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 283.9 | 51 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1608.5666 | 107 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 250.4833 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.4999 | 93 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 544 | 68 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2882.6 | 812 | 1 | 1 | 0250-Pulverizer feeders | SF-Startup Failure | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1448.3999 | 153 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.2167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.5 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.8333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.0667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.5833 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13.75 | 55 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.7583 | 19.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.2 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.2 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.5 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.048 | 53.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25 | 100 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.38 | 25.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.2 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.8 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.7333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.2499 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 86.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.5333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 106.2746 | 72.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.2 | 34.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 139.9999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.95 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158.3999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 182.4 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 194.4 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.5333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 198 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.4 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 332.0408 | 63.65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 372.5166 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 392.35 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 444 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 470 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 497.25 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 529.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 585 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 596.9333 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 622.7 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 627.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 680.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 692.6333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 724.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 767.6666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 788.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1076.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1115.1999 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1129.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1234.737 | 130.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1237.3333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1240 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1275 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1281.3333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1325.8666 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1533.84 | 199.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1535.9666 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1692.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1925.1 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2947.5832 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.71667 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.895 | 23.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.4 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.4 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.6666 | 100 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.1667 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.9333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.45 | 9.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.8332 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.8981 | 48.19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.9 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.6666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.8566 | 68.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.8833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.1667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.4 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.9999 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.36 | 57.36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 96.6167 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98.1666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99.75 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.25 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.8 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111.65 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.5 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.7833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 157.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.3333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 168.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177.0666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189.28 | 33.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215.1 | 57.36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 247 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 251.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 282.3333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 284.1959 | 193.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 290.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 300.6666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 310 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 330 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 342.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 382.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 390.7166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 407.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 462 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 481.4166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 502.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 586.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 773.5 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 966 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1076.25 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2473.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.95 | 3 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.65 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2.1833 | 65.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.5333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.8333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.7533 | 53.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13 | 52 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.8 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 17.25 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.85 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.68 | 42.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.0999 | 189 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.3333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45.9 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.2166 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.0166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.5333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.1333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.5833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 102.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 105.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 106.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 127.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129.6 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 131.1333 | 112.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 147.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 169.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.6 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.5999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 202.6666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229.9 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 231.896 | 165.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 243.5832 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 255.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 255.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 281.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 284.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 296.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 301.5 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 323.7 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 347.0167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 369.2333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 416.5 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 427.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 441.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 556.5666 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 568.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 645 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 704.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 750.8333 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 756 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 978.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1014 | 338 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2142.0666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4375 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5583.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.2833 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 88.3333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98.01 | 32.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 109.15 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 484.1416 | 70.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 741.8666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1109.9666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54.6667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2956.98 | 227.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9.35 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 46.4667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 341.85 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 633.15 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 138.775 | 21.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.08 | 43.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.475 | 14.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.995 | 39.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.1 | 4.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.74 | 74.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.755 | 41.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 374.1249 | 109.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.465 | 23.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.6933 | 25.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.52 | 14.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.8333 | 29.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.85 | 25.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57.75 | 63 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.5333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1050 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.3999 | 132 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 605.7333 | 154 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 94.9666 | 37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1122.0474 | 99.15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.4999 | 270 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.8332 | 149 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 68 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 98.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 383.4166 | 215 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 231.2 | 48 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 875.6165 | 491 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 58.3333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 18.3667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 90.6667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 1.5667 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 20.7667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 0.66667 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 5.8333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 52.8 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 64.9 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 107.2 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 111.65 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 143.85 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 624.2166 | 67 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 20.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 932 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 135.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1.2833 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 8.9167 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 10.0667 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 16.7833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 9.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 115 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 2.4 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 7.6 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 39.8667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 43.3833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1.4333 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 16.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 42.3666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 83.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 842.8333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1.65 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 148.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 60 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 48 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 3.0667 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 53.4333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2464 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 0.36667 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 105 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 140.4 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 5.4667 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 13.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 13.95 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 3.6667 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 6.2667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 11.9 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 406.4 | 50.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 15 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 4.8 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 6.1 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 9.5 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 7.05 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 7.55 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 25.7333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 178.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 0.9 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 4.5833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 5.9333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 11.2 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 101.0167 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 4.1667 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 21 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 280 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 6.05 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3.0333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3.85 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 6.4167 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 42.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 20.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 4.2 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 18.9333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 8.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 89.95 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1.8333 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 6.2333 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 30.1 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 180.4 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3.4833 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 4.6667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 29.3333 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3.3 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 5.6 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7.3333 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 11.4333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 315 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 5.95 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 13.9333 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 4.8 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 5.3167 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 6.05 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 9.3333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 11.0833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 17.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 14 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 356.65 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 5.6833 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 5.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 6.7833 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 21 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 336 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 14.35 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 19.25 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 284.05 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3.25 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 4.2167 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 15.2 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 22 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 36.9 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 168.6666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 315.9 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 537.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 326.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 733.3333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 100 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 207.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 547.0666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 99.7333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 16 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 36 | 18 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6.3 | 42 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132 | 24 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 189.7499 | 99 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 577.5 | 99 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 711.2166 | 139 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 888.5667 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 8.3333 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 22.6666 | 80 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.8333 | 25 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161 | 69 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 321.95 | 137 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 362.5 | 145 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 461.8999 | 93 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 231.8666 | 94 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1.4 | 7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.5 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 371.25 | 99 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 499.95 | 99 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1435 | 75 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 58.85 | 107 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 113.5833 | 47 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.8333 | 91 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 211.2 | 96 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 885.7333 | 52 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1118.6666 | 40 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48 | 32 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174.1666 | 55 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 38.5 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 15 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63.3333 | 190 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.5 | 10 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 213.5 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 239.9999 | 90 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1144 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 10.8 | 72 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.75 | 35 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 997.9999 | 120 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1000 | 160 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 963.3332 | 170 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3642.9167 | 35 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 336.9166 | 65 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 459.4825 | 79.91 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 127.46 | 63.73 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1438.75 | 25 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3282.5 | 202 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9 | 90 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.6666 | 175 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 152 | 76 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 276.4999 | 210 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 370.5 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.9667 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.1166 | 89 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 0.91666 | 5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1485 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 433.1 | 71 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 784.3333 | 130 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 119.1667 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 139.9833 | 37 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 150.1666 | 85 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 32.9666 | 86 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 511.2 | 71 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.3667 | 14 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.3333 | 10 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.1667 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 155.1667 | 38 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2126.7333 | 38 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 114.2 | 91.36 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130.4167 | 25 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 773 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91 | 15 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 133.0333 | 26 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 146.4 | 24 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.6666 | 170 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 224.1999 | 114 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320 | 96 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 479.9666 | 34 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 910.5666 | 118 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.4166 | 47.5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.6 | 54 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.75 | 15 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121.6333 | 89 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.6665 | 235 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.5 | 27 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 97.5 | 75 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 125.1 | 139 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 342 | 57 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5.7 | 57 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.3333 | 95 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 64.1333 | 52 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 108 | 240 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 453.8499 | 87 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 567.9166 | 145 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 619.7333 | 112 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6920 | 80 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100.2 | 36 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 430.65 | 99 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 21.2667 | 22 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 800-Miscellaneous
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 15.565 | 84.9 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 178.6667 | 16 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 420.3333 | 130 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66.9584 | 81.99 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 25.645 | 66.9 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 689.9999 | 90 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1216 | 76 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 385.2 | 54 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10.9998 | 21.29 | 1 | 1 | 0255-Pulverizer feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 312.4783 | 59.9 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1243.3333 | 50 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61 | 61 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 632.1166 | 97 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 19.215 | 54.9 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 30.7533 | 65.9 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 278.3333 | 50 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 533.4 | 63 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.1666 | 62 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 62.1063 | 86.66 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129.2666 | 28 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 766.6666 | 115 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 196 | 28 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 413 | 59 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62 | 62 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 209.7666 | 89.9 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 24.248 | 51.96 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.0666 | 94 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 133.9 | 103 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 72.5616 | 66.98 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 120 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 33.25 | 52.5 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 114.8083 | 59.9 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 220 | 55 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 11.6667 | 20 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 16.646 | 47.56 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 208 | 52 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 860 | Co-generator Block | RFC | Summer | 484.1666 | 166 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 860-Co-generator Block
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 860 | Co-generator Block | RFC | Winter | 262.3 | 129 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 860-Co-generator Block
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.53 | 61.8 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 559.2999 | 141 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1225.9999 | 120 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 309.1665 | 530 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.5373 | 41.96 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.3333 | 125 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 138.2499 | 105 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 585 | 90 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1801.4666 | 118 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.25 | 5 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.45 | 71 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55.2 | 46 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97.4666 | 68 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 291.6666 | 70 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1397.5 | 215 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390.3666 | 98 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1066.64 | 107.2 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 90 | 90 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 624 | 65 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1968 | 82 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 96 | 32 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.75 | 7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.5 | 41 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170 | 17 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 185.256 | 14.88 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196 | 14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 336 | 42 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 597.3333 | 160 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1739.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40864.0833 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.6667 | 22 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.9166 | 61 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191.9167 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 316.2 | 102 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1632 | 34 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 85 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 110.25 | 147 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 462.5 | 75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 649.1667 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1076.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1462.8 | 318 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1513 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2508.75 | 135 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 253.7 | 43 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.825 | 25.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.1433 | 73.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 680.4 | 48.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 981.8666 | 28 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1191.87 | 77.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1881.5 | 42.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40.6667 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70.4 | 6.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91.77 | 17.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138.6 | 4.2 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 239.1999 | 78 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.7495 | 675 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5624.9991 | 1350 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 0.75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.5 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77 | 14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 167.2 | 19 | 1 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 193.5999 | 96 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 213.5167 | 11.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 229.9 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1112.5 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1175 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17969.8633 | 99.4 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.7125 | 0.25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 484.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 770 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1183.3333 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1464.8333 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6265 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.6666 | 167 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4094.75 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5181.75 | 135 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19764 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 33.1333 | 7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.7917 | 2.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 363.22 | 3.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129.36 | 30.8 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1892.8333 | 27.7 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 128.0667 | 22.6 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2185 | 95 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5114 | 30 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 599.3333 | 116 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5227.25 | 515 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 570 | 570 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4705.9997 | 780 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 4 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.4 | 3 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.5667 | 17 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 136.75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 167.8333 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 330.6 | 87 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 567 | 27 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 864 | 576 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1260 | 63 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1546.6666 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1653.5665 | 226 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1829.1665 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.25 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 249.1666 | 65 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 275 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3489.9999 | 300 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9506.6665 | 310 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54.1666 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57 | 114 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 82.4 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.7 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 156.95 | 43 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229.1666 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 272 | 108.8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 349.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 399.3166 | 97 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 639.3332 | 140 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 839.7333 | 18.8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 993.9999 | 210 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1800.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2460 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3360 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25943.9998 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.6067 | 23.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.305 | 9.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4062.5 | 650 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 442.4998 | 450 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.5 | 9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.6 | 18 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.6973 | 19.91 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 288 | 96 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 288.1667 | 14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 303.3332 | 182 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312 | 65 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 371.2 | 29 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 497 | 42 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 517.3333 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 675 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 811.25 | 147.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4000.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4487.5 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.3333 | 16 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.4666 | 31 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 171.9998 | 240 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.1667 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 300.5167 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 349.6 | 152 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 676.0831 | 305 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13641.8333 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34179.6 | 364 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 159.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 220 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 402.7666 | 43 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 408 | 272 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 467.25 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 486.8332 | 230 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7427.9999 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8546.8333 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 5.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.8 | 3.2 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260 | 32.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 676.2 | 29.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2103.5633 | 92.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2310.4 | 6.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4951.8583 | 46.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1071.5833 | 55 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 413.7865 | 210.4 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.8 | 12 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 103.5 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 103.8007 | 26.39 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.6833 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2467.5 | 105 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7973.5327 | 28.73 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15668.3333 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.2 | 12 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222.1666 | 31 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 291.6 | 36 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 610.5 | 370 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 900 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69499.9998 | 300 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.0833 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 220.8333 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 274 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 357.6666 | 74 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 483 | 420 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 513.895 | 23.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1268.75 | 87 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1800 | 75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55517.9998 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.008 | 23.64 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330.4 | 5.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2070.6133 | 25.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6167 | 7 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.0667 | 17.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246.5333 | 86 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1449.9165 | 635 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 265.5353 | 513.94 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8505 | 150 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | TRE | Off-Peak | 1862.7667 | 47 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.4167 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 113.75 | 105 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.845 | 43.58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140.25 | 51 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159.9167 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 187 | 51 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 314.9392 | 25.85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 591 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 690.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38409.8166 | 99.4 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 62940.3332 | 310 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134.5833 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.5 | 47.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 411.3667 | 14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2252.5 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4303.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4684 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6918 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18217.9833 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.3333 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 119 | 23.8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 661.7333 | 56 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 669.1667 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1563.9167 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2144.0833 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33869.9166 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 76.4167 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.9 | 23 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.955 | 42.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 427.7 | 4.7 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 617.6 | 19.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 609.4833 | 97 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3100.5 | 585 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.0166 | 53 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.85 | 87 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 301.4667 | 14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 436.6667 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 469.2 | 46 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 716.25 | 143.25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 999.4166 | 67 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2213.3925 | 14.85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8642.83 | 99.4 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11190 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3875 | 12.75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.2 | 32 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 217.5 | 290 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 284.2667 | 32 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 627.1999 | 147 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 677 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 724.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2607.7332 | 508 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3875 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5153.4166 | 335 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.3333 | 56 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 242.0833 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 338.8666 | 46 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1386.4999 | 177 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1820 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44 | 22 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262.5733 | 37.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 298.3 | 19 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114.4583 | 33.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 145.8333 | 70 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 25 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 586.25 | 37.5 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1564 | 340 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12916.3996 | 588 | 1 | 1 | 0260-Primary air fan | U2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 166.25 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245 | 14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 358.4166 | 115 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 773.4999 | 105 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1924 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3624.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3901.5 | 578 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6564.5 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7798.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.8833 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180 | 9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 237.5 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 910.35 | 119 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3009.0665 | 217 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17994.9999 | 354 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 905 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4532.9166 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.4 | 15.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 604.8 | 18.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 573.6 | 23.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1003 | 590 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 5907.4165 | 247 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 233.5667 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 4421.3664 | 335.8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 668.3333 | 50 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 5133.3333 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.75 | 147 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 344 | 172 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.7716 | 123.1 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.25 | 75 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1492.25 | 127 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282.9167 | 25 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.6667 | 8 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2177.5 | 335 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 221 | 78 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 494.0833 | 55 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1880.8666 | 317 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.4667 | 16 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 408.333 | 500 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2952.9 | 386 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3105 | 460 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 195 | 100 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 650-Fluidized Bed
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 456 | 19 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26.8333 | 23 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38 | 19 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78 | 60 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139.5 | 90 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4120 | 100 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 346 | 346 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3181.2 | 132 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109.6667 | 35 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.9 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1540 | 350 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 436.15 | 33 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10085.6661 | 790 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.0833 | 35 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1261.5 | 45 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4484 | 95 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1600 | 75 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.5767 | 3.4 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 110.5 | 130 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12372.75 | 585 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120.95 | 123 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132.0833 | 25 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5301.3332 | 355 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.25 | 15 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 149.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 171.5499 | 219 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8024 | 472 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 558 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6249.5665 | 626 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.58333 | 7 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 232.9166 | 215 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 194.75 | 19 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 293.3333 | 100 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19544.6332 | 481 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 680 | 272 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 401.6667 | 50 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1117.8 | 81 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1830.3333 | 95 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.8667 | 22 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.75 | 47.5 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.8333 | 50 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2883.9997 | 420 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8204.0999 | 207 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 172.3333 | 110 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 843.75 | 45 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16.4667 | 4 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24 | 80 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.0667 | 11 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1850.3331 | 610 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 351.6666 | 100 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18706.6664 | 400 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1847.3 | 87 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2107 | 301 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3307.5 | 105 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13580 | 485 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34.8333 | 55 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7200 | 750 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6279.4996 | 570 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 2.5 | 10 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 650-Fluidized Bed
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2.9013 | 0.64 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.8833 | 13 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.5 | 15 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225 | 225 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2880 | 360 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.4329 | 674 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320 | 80 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1125 | 225 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2583.3333 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 197.7033 | 51.8 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7120 | 80 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.8333 | 35 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210 | 12 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220 | 22 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 402.5 | 25 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 516.75 | 39 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1184.5 | 23 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2333.8333 | 55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 717.23 | 5.1 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60 | 60 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 120 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 6 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.8373 | 21.41 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 252.9999 | 165 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 465.5966 | 60.73 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1134 | 28 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4908.3665 | 482 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5152.5833 | 77 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17101.5833 | 35 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127.0333 | 103 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.5 | 65 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1246.5 | 277 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2356.9 | 481 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2850.8333 | 55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11059.5833 | 55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 725.9998 | 360 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.5 | 2 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.5 | 5 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 352.3331 | 302 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 638.6666 | 80 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.53333 | 4 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.25 | 41 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.0023 | 20.53 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84.25 | 15 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 432 | 96 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1410.038 | 40.02 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1430.6666 | 80 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1828.6666 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7770.75 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.3333 | 16 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.3333 | 70 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 420.2666 | 197 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3921.25 | 75 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.3233 | 5.8 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1454.18 | 36.4 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 240 | 240 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 300 | 300 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8787.5 | 370 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1293.7495 | 675 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320.0832 | 167 | 1 | 2 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 364.1666 | 46 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 525 | 105 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 263.0833 | 77 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1359.5833 | 65 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3247.1 | 57 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 208.3962 | 204.98 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4885.8332 | 550 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 20 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 36 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.6667 | 20 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130.1667 | 22 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164.2166 | 167 | 1 | 2 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47 | 15 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160.8666 | 127 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1704.1665 | 250 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 290.9667 | 14 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.2 | 10.8 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180 | 180 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15840 | 60 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5060.1665 | 626 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.2 | 96 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 541.6666 | 65 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 612.5 | 250 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.5 | 10 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 549.0833 | 55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26802.5 | 150 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1332 | 148 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.184 | 3.98 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 125.4633 | 5.66 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.048 | 0.24 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.264 | 0.72 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.159 | 0.53 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.198 | 0.66 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 82 | 102.5 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.006667 | 0.04 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.194 | 4.66 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 10.7003 | 0.94 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 58.8743 | 3.47 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.30767 | 0.26 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.71333 | 2.14 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.206 | 2.01 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Winter | 35.875 | 102.5 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.021667 | 0.26 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.03 | 0.09 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 0.04 | 0.3 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 11.1907 | 0.77 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 37.59 | 35.8 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.8107 | 1.94 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 860 | Co-generator Block | RFC | Winter | 182 | 24 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 860-Co-generator Block
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55.3333 | 166 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7.5 | 50 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75125.1663 | 490 | 1 | 1 | 0265-Primary air heater | U2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 442.5 | 118 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1699.3333 | 40 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 35 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 443.75 | 25 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 479.5833 | 25 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 583.7666 | 166 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14215.6 | 6 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.75 | 11 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76 | 95 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.3493 | 52.94 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 375 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 288.75 | 165 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.1667 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 228.3333 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.4167 | 5 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.6667 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.0833 | 41 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.6 | 54 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168.7666 | 122 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1971.69 | 172.2 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 183 | 183 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1060 | 120 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 417.0665 | 184 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 111.8 | 43 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1460.2498 | 297 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.5167 | 23 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.7667 | 14 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.8 | 36 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.682 | 34.92 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 227 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 376 | 80 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.6666 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186 | 72 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 261.6667 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 510 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.11 | 11.4 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1169.6666 | 116 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2406.3996 | 564 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119 | 119 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7176.1998 | 318 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8547.5 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170.6666 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 368 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 516.25 | 35 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 949.3333 | 160 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 229.5 | 54 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.5 | 14 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3380 | 325 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 217.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 433.1833 | 47 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 639.6665 | 202 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 480 | 120 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 407.7333 | 88 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.3333 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.3126 | 57.22 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2016.6667 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 111.9332 | 146 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 94.6266 | 141.94 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 858.7 | 6 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95.7 | 33 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 373.3332 | 200 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.2666 | 28 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 120 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 435.5666 | 146 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 421.2 | 78 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 575 | 230 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1920 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3223.112 | 79.78 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5284.9998 | 300 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.875 | 14.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160.4666 | 116 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 185.5933 | 38.8 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 226.4 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230 | 46 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 553.35 | 119 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1885.6 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 193.5 | 129 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 237.5323 | 112.22 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 298.0833 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 328.5333 | 22 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 570 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98.852 | 38.02 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.743 | 24.33 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 624.8 | 28.4 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.9667 | 26 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 64 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3110 | 622 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1080 | 270 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.4 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.1667 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.5 | 19 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 298.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 868.4166 | 85 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1408 | 176 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2170.6664 | 370 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.8333 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 248.9999 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 283.5667 | 47 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 404.8 | 33 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 903 | 86 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.5417 | 10.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.125 | 5.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 110.565 | 170.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110.9166 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 195 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 291.6665 | 250 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 538.2958 | 10.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1502.6664 | 460 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 555.8332 | 230 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3860 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.8333 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 106.5999 | 123 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 92.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7389.75 | 835 | 1 | 1 | 0270-Primary air duct and dampers | SF-Startup Failure | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 273.6 | 342 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18004.4999 | 270 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.0833 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.7999 | 87 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 230.125 | 65.75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 530.8333 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 756.25 | 125 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 895.5 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3465 | 330 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4035.4166 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.6 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 177.125 | 9.75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 263.3333 | 79 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 347.0999 | 117 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1474.4633 | 117.8 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.1167 | 23 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.395 | 148.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 107.25 | 5.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 163.3333 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.6667 | 10.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 188.7534 | 159.51 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 222.5 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 312.3749 | 157.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 359.1667 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 376 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 495 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1200 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5034.5666 | 146 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 593.3 | 51 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1062.4998 | 510 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102.3 | 99 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 472.5 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 573.8666 | 269 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1030.108 | 97.18 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1052.3333 | 82 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.5 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210.9333 | 113 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 511.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.5 | 105 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 63.602 | 21.56 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 233.3333 | 56 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 293.6999 | 99 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 214.4166 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45.2666 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.2 | 54 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 21.5333 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.5 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1509.75 | 135 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2529.3333 | 80 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.06 | 26.8 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 238.3333 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 380 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 630 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 636.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 664.3333 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 769.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.4166 | 85 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.5 | 22 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.5 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.125 | 14.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.9333 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.756 | 93.84 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 367.5 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1304.6667 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2041.6666 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13838.9333 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.25 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.8333 | 5.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 145.9165 | 515 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 188.5333 | 101 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 223.75 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 925 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1987.0833 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2560 | 160 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10622 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.7333 | 13 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.7 | 17 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 57 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1120.9998 | 228 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6751.2497 | 825 | 1 | 1 | 0270-Primary air duct and dampers | SF-Startup Failure | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52333.9995 | 822 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5339.0831 | 395 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 162.5 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 313.1333 | 44 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 478.7475 | 91.19 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1757.3333 | 160 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1768.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3624.4999 | 165 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6382.75 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.9166 | 85 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 267.4666 | 118 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 479.9666 | 119 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.9792 | 10.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.75 | 0.75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 95 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 581.25 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 746.6666 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1060.5 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1132 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2500.8333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.0166 | 31 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1171.6 | 232 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 342.8333 | 85 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31088.7497 | 825 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 231.9166 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 321 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 660 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 724.3333 | 82 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1038.75 | 138.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1856.5 | 94 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.7667 | 22 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.9 | 22 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.5333 | 84.8 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.4667 | 8 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 374.9999 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 420 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4255.2 | 72 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.7708 | 10.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 35.2055 | 57.09 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99.1667 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 109.4163 | 505 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130.1667 | 5.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.75 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 254.9167 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 534.9167 | 24.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4796 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.0667 | 29 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.3333 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 389.7383 | 37.9 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2444.0833 | 211 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.6667 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34645.6 | 682 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17764.9997 | 825 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.8333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127.204 | 25.96 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 322.6666 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3778.8 | 24 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.8175 | 95.15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.5833 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.4 | 84 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.7183 | 157.45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 181.25 | 14.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 298.3333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 376.8333 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 425.7 | 86 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 667 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1812.5 | 145 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2553 | 148 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2575 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8189.35 | 293 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.4083 | 5.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.75 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 240 | 32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300.5333 | 98 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 385.25 | 67 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 600 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 639.5333 | 106 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 926.1833 | 61 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.25 | 19 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 103.7208 | 85.25 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.25 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26470.4163 | 505 | 1 | 1 | 0270-Primary air duct and dampers | SF-Startup Failure | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 20 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 650-Fluidized Bed
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 4853.375 | 102.5 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 650-Fluidized Bed
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 22.1667 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 650-Fluidized Bed
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2025.3333 | 196 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 650-Fluidized Bed
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3333 | 19 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.1667 | 26 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 260.8666 | 52 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 372 | 240 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468 | 240 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 906.3 | 57 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1919 | 202 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11938.2166 | 79 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.0333 | 73 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81.25 | 75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 784.7 | 118 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2397.8 | 114 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3960.0448 | 52.37 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60 | 72 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 558 | 90 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198.1833 | 47 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 688.5 | 85 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.35 | 9 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.15 | 57 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.6666 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.8833 | 67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 688 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.5 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21 | 18 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85.55 | 29 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.3142 | 160.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 627.75 | 81 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1680 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 443.3 | 66 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 538.9863 | 60.11 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 826.6666 | 155 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1082.1666 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1218.3333 | 68 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1400 | 175 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.4 | 57 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.995 | 39.27 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 839.5 | 23 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2678.6665 | 205 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.2205 | 43.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.5395 | 38.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 86 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.5235 | 43.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105.1333 | 83 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 116.7525 | 155.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139.1667 | 25 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 283 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 610.1666 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54.78 | 33.2 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 250.75 | 85 | 1 | 1 | 0280-Pulverizer fires | D3-Forced - Postponed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.5875 | 43.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.4166 | 89 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111.4667 | 32 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 860.1833 | 73 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1626.8333 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7042 | 280 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 344.5 | 53 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11.6666 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.1133 | 34.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 169.0605 | 53.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 610.8333 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 966 | 105 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.6 | 73 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.7833 | 19 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.7 | 66 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 82.5 | 18 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 467.6666 | 230 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1516.6664 | 325 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14777.6666 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10.1333 | 38 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 347.5 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4765 | 75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.9167 | 17.5 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 132.6 | 22.1 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27187.3332 | 520 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.5233 | 12.2 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 64 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.8333 | 35 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 194.7 | 66 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 222 | 20 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 443.3332 | 140 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 820.3333 | 92 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1159.9499 | 99 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7613.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.6666 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1288 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27.3 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29.246 | 62.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 66.6666 | 80 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 767.5 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.9666 | 73 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82512 | 540 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.0675 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 339.7 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 343.0666 | 31 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 797.05 | 57 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2065.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3655 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.6 | 36 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185.0833 | 5 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1054.4 | 96 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.3666 | 46 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195.7568 | 52.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 772.5833 | 127 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1193.5 | 70 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.4333 | 22 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.3 | 26 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.357 | 104.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.972 | 106.74 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520.5333 | 61 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3712.5 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7363.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125.398 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238.8166 | 161 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 353.3333 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 803 | 55 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3055.0666 | 88 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.7 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 170.313 | 43.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 212.3666 | 46 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 413.8333 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 806.954 | 276.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1233.1 | 118 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1516.6666 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2886.3999 | 123 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3937.3698 | 262.2 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12822.8333 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1315.35 | 79 | 1 | 1 | 0280-Pulverizer fires | D3-Forced - Postponed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9440.8965 | 216.7 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 116.6666 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 140 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.4 | 66 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 238.75 | 75 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 246.9333 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276.7333 | 28 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 516.6666 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640.8 | 72 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.2 | 23 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.95 | 23 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 208.5333 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 445.5 | 162 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1014 | 78 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2818.75 | 75 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6428.5 | 115 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14818.5 | 30 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.3 | 27 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 771.5 | 30 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2008.6 | 242 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3494.6 | 34.6 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 50 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 425.35 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 455.6 | 51 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 573.6 | 36 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 616.9 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 887.5167 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1252.5333 | 56 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1267.2 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13008.6667 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206.25 | 15 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 177.1 | 66 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437.25 | 53 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1039.65 | 87 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2091.75 | 45 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 317.4833 | 43 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 426.8332 | 197 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 546.6666 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 610.7 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 799 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 828.0999 | 78 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 896.25 | 75 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1150.2667 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1382.4 | 128 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9004.4167 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34840 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5908 | 35 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 328.2333 | 86 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3053.2499 | 135 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 542.6666 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1057.0999 | 93 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 218.8833 | 23 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 245.3333 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1248.8667 | 13 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1290 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1379.9999 | 207 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2256 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2259.1333 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2552.8833 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2921.6667 | 20 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3640 | 35 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.2 | 10.8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11664.75 | 45 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13297.5 | 45 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.1666 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.5666 | 37 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 390.05 | 87 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 827.5666 | 74 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 852 | 71 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 883.5 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 962.4 | 36 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.7833 | 79 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 715.1333 | 68 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2375 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48925 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 167.3333 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 621 | 207 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 985.8 | 212 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 997.3333 | 187 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1156.0332 | 158 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1944.2333 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 430.6666 | 136 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2889.2 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6056.3666 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1363.3333 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6990 | 30 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 236.6666 | 142 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 259.2 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 577.0999 | 174 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4336.5 | 45 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 179.8 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.6666 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 867.7333 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1057.3333 | 80 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2665.25 | 105 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2984.3 | 66 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19873 | 70 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43617.3333 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.3333 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 306.6667 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1742.9167 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1919.4667 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 960 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3320.8333 | 50 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 524.9 | 87 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 534.3666 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 674.4666 | 67 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 724.8833 | 31 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1005.3 | 27 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.2 | 78 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36750 | 35 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.95 | 57 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.3 | 31 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195.2 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 521.0667 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 990.1333 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 356 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31720 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64800 | 50 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.3 | 9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 91.35 | 27 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 267.75 | 63 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 932.75 | 105 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4961 | 22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.4167 | 5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.25 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.2667 | 8 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 165.3332 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 205.8333 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 417.9166 | 59 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1389.6666 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5172.5 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12251.6666 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 119.6541 | 152.75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256 | 160 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 306.25 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 407.9333 | 211 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 470.1333 | 82 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1482.2498 | 231 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3199.6666 | 145 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 252 | 36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2646 | 189 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 183.7 | 22 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 833.25 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.4667 | 8 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.75 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 253 | 33 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 349.5833 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 988 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6032.5 | 127 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.75 | 51 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.75 | 55 | 1 | 4 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1425 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1488 | 160 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12184.7 | 57 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.25 | 53 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70.6666 | 53 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 275 | 66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 399.3 | 66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 623.3333 | 88 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 691.1666 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2448 | 204 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4672.5 | 175 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5235.9998 | 231 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 162.9166 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1213.85 | 110.35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1717 | 101 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21.9333 | 94 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160 | 16 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 184 | 230 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 269.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 344.1667 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 456.1666 | 119 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 949.2 | 4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1047.4999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3273.8333 | 130 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5899.9998 | 300 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.6666 | 68 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.6667 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 664.2 | 41 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 674.6665 | 184 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6675 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.5988 | 6.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 115.1745 | 15.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 298.1499 | 201 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 350 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 615.4166 | 175 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1172.4999 | 105 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 368.75 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15109.6166 | 67 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2452 | 16 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1009.6875 | 18.75 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10228 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 304.2666 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3333 | 5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.4333 | 109 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.5 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 102.2809 | 133.41 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 181.8 | 12 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 815 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1414.8333 | 130 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12087.5333 | 53 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.75 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.25 | 45 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.5 | 50 | 1 | 3 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.325 | 60.25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 270 | 270 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 345.8333 | 250 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 472.7833 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1048.8 | 76 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2646.0833 | 113 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41.5166 | 53 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 229.5 | 102 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 349.0666 | 88 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 940.4 | 8 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1093.75 | 175 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1285.2 | 126 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 91.466 | 144.42 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14877.52 | 52.08 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20833.1666 | 51.02 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 179.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 218 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 229.5 | 102 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 776.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1105.4165 | 175 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.75 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.5 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144.375 | 17.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 310.75 | 113 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 11716.25 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.75 | 23 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.1683 | 48.85 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29 | 87 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 74.6666 | 112 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 221.6333 | 109 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 256 | 32 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 532.8624 | 136.05 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 321.25 | 128.5 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 620 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.4333 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.6667 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.2 | 22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.4027 | 16.64 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 258 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 370 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 408.9167 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1242.1333 | 32 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 409.5 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 484.95 | 9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2135.9166 | 95 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2301 | 118 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3894.9999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4344.9999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5075 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.8 | 51 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 168.7137 | 15.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 310 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 376.0166 | 77 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 505.5 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 704 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1278.6667 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26 | 13 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154.3133 | 31.6 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1094.9199 | 74.4 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1031.8 | 77 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1732.1166 | 103 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21904.5 | 102 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.5 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.1666 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 894.6667 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1400 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1675.8 | 147 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1723.5832 | 185 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2733.75 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5560.5 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.2885 | 15.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.5 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60.4166 | 145 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 136.6667 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 283.5 | 42 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 350 | 200 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 659.9682 | 15.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1122 | 187 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4745.5666 | 118 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 106.3333 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 912.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4710 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1380 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2173.875 | 51.15 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.4167 | 5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.4 | 57 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 212.75 | 23 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 281.6666 | 130 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4637.9333 | 73 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.75 | 67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 70.855 | 11.1 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198.45 | 147 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1577.55 | 117 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 211.0227 | 15.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2754.9 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10303.3333 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12765.5 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2610.8333 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1260 | 18 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.75 | 18.75 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 158.3333 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1610 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 222 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 650-Fluidized Bed
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 67.6666 | 58 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 227.5 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 150 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 542.6666 | 88 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1287 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 103.5 | 18 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 684.4166 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 860 | Co-generator Block | RFC | Off-Peak | 1239.4999 | 111 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 860-Co-generator Block
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.7167 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.25 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.88 | 37.32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.5 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51 | 68 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.05 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.8333 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 134.7333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 137.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162.7666 | 257 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 177.565 | 62.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 183.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 185.1667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 191.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 228 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 252 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 340.4 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 344.4 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400.4166 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 496.9166 | 89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 538.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 544.1333 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 562.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 657.5833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 665.95 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 737.4999 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 756.5 | 178 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 976.5 | 217 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1103.325 | 23.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1178.629 | 114.43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1267.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1513.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1821.8333 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1892 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2594.4 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4087.7999 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4427.2666 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4709 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7862.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13338.5 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.9667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 14.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.4167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.5 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.4166 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 100 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 160.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.5 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 195.8332 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.1666 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 279.0666 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 371.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 405.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 445.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 485.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 579.3333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 612.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 904.6666 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 998.6666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1044 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1049.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1262.4 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1265 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1396.8333 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1692 | 235 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2200 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2973.9333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4351.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8441.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19602.5333 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 31.29 | 29.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.6166 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 49.2 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 77.14 | 34.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 142.97 | 84.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145.75 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 151.0667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 155.8333 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158.3332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 196.35 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 203.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 313.3332 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 336.8333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 346.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 413.2583 | 49.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 488.25 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 718.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 817.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1046.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1055.25 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1106.1133 | 39.98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1213.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1579.2 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1702.9999 | 393 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4560.8333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5212.5 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 6127.88 | 20.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.6 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 177.3 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.6 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 204.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4.8 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 183.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 554.4 | 154 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.0433 | 13.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.54 | 46.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.4 | 42 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.6 | 15.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1687.2 | 70.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11800.45 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.8 | 4.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 444.4666 | 113 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.8667 | 22 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2300.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 166.708 | 140.88 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33.8333 | 145 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128 | 160 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 770.9166 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 786.8 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.5 | 41 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63 | 84 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105 | 105 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 281.8333 | 89 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5586.4826 | 61.48 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2500 | 100 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8520.6331 | 742 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7568 | 352 | 1 | 1 | 0310-Pulverizer mills | U2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.5 | 6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 18.375 | 44.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 40 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23.3333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.8333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.7791 | 90.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.4666 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.4666 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66.5833 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 79 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 90 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107.6667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 109.175 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111.6137 | 136.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.4167 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 124.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 137.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 149.4666 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 157.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 174 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 182.2333 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 188.7333 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 303.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 308.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 316.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 336.6835 | 66.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 365.0833 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 429.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 446.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.7165 | 278.01 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 517.05 | 383 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 552.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 552.75 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 688.8694 | 164.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 735.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 941.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1000.1333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1052.3413 | 151.78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1260 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1562.6331 | 362 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2837.3 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8815.6606 | 143.89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9541.35 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10637.5 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.5 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.05 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.4833 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.05 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 85.72 | 42.86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89 | 89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.05 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140.8 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 152.38 | 152.38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 217.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 229.95 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 241.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287.1332 | 146 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 291.6662 | 700 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 344.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 354.6666 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 358.3827 | 16.49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 388 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 430.5 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 442.05 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 503.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 529.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 531.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 532 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 575.05 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 851.58 | 33.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 882 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 965.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1183.8667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1624.9333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1806.7955 | 24.51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.8126 | 53.17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.95 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.3333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.75 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.1666 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.8666 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100.2667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 128.05 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 131.75 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 141.6667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.2833 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 147.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 177.6666 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 255 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 270.1 | 146 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 317.9167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 319.5 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 331.3332 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 434 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 465 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 478.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 496.6333 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 743.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 770 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 898 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 939.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1181.4 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1481.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1748.4 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1900.3667 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2962.6667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4236.016 | 80.84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10615 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 463.6833 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.2 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 135.4166 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 166 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 439.8333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.6 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332.35 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 428.5666 | 86 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 474.5 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 687.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 728 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.3283 | 26.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.3333 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.5 | 10.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.5633 | 3.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.9 | 42 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 327.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 536 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 590.525 | 39.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4071.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4653 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120.375 | 22.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 284.1666 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 333.5 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 462.055 | 51.15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 234.4 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 269.1666 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 272.9167 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 682 | 124 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1558.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1824 | 190 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26.5 | 265 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 104.8 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 326.5166 | 137 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 518 | 370 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3696.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.36 | 64.72 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.4833 | 64.45 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 943.8 | 11 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 225 | 75 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 244.8366 | 149.9 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12840.8997 | 414 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3131.333 | 440 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1690.1498 | 231 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.28 | 42.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.6833 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.7 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.75 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.45 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.8 | 4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.2667 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.5999 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.5333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121 | 2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.6 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.75 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 147 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.75 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.3333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 158.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.35 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.4333 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 202.6666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 226.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 243.8333 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255.5 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 256 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 299 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 304 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 309.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 337.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 351.3333 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 356.4 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 398.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 419.3333 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 441.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 470.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 505.4 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 565.5666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 595.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 615.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 645.8333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 710.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 782.75 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 849.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 850.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 932.1666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 999.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1400 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2021.2499 | 225 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2182.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2224.6666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2240.9399 | 79.56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2245.1333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2347.65 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2727.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4781.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14070 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55836 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.6675 | 3.93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.6999 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 40 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76.0833 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121.9166 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.35 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 191.6665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.9166 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 248.2666 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 506.3333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 553.15 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 573.3 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 694.9998 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 700 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 825 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1283.25 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.1833 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.0003 | 5.18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27.0833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.2667 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46.0833 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.1 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 149.5 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 173.2243 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 197.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230.6333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 292.1833 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 296.8665 | 244 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 430 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 522.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 640.8 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 750.832 | 44.96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1017.4332 | 466 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1106.85 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1497.408 | 63.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1654.3999 | 192 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8201.5 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 65.3666 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.6 | 24.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.75 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.9 | 28.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50 | 2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.7917 | 14.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160.4667 | 29 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 243.5833 | 79 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 451 | 66 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 310.2999 | 87 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 398 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1155 | 231 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1899.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18411.4 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.94 | 19.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.6167 | 23 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 69.3 | 22 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.725 | 51.15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.4317 | 4.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84.8667 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 167.1666 | 170 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.55 | 47 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 97.5333 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 168 | 72 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 218.1667 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 380.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 526.0332 | 367 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 426.7666 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1002.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9122.05 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.75 | 97 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78 | 78 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 40.8 | 48 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 249.3333 | 85 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 725.9166 | 155 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 739.0832 | 245 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14140.0583 | 156.1 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.2 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.3425 | 28.65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.8 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.9333 | 4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.3332 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.6422 | 30.77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.1333 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.5 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.55 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.4833 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136.5 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162.75 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 171 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 192.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 212.2328 | 66.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 223.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246.2333 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 275.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 279 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 292.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 312 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 519.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 522.4833 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 617.6667 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 711.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 761.2 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 765 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 946.4 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1010.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1118.9735 | 117.17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1247.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1334.1666 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1391.5 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1419.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1489.5831 | 275 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1862.4666 | 182 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1917.85 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2300.9 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.8667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9.3333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.6 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.7333 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.8333 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.6 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85.1088 | 35.71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.5 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.3 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127.8 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168.9 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186.25 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196.3332 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 257.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 302.9833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 355.35 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 486.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 620.4 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 690 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 900 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1196 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1369.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1511.8333 | 193 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.3667 | 23 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.7333 | 10.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 34.5 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.15 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.8666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 50.5093 | 29.14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 63.25 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.6 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.6 | 168 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 77.4666 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 104.4 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.8 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153.433 | 219.19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 159.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 182.32 | 42.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 190.19 | 41.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 199.3332 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 234.1667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 274.2667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 287.95 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290.275 | 13.66 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 320.2333 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 383.5 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 483.75 | 225 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 521.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 595 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 621.1833 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 628.8333 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 653.3333 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 784.1167 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 978.1316 | 40.06 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1395.1 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2240 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2270.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3495 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4783.3499 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6411.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 137.6 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138.7 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1172 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.5666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 102.4 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 131.8666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 242.45 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 36 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.2 | 3.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 218.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287.86 | 38.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 336.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 702 | 58.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1450 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.38 | 25.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1098.7666 | 119 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35997.5 | 77 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.9866 | 29.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.3333 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3769.8 | 61 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 182.5633 | 168.52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 200.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 347 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5645.5665 | 178 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20 | 20 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.7883 | 51.02 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296.6666 | 89 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 789.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 396 | 99 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 528.4499 | 117 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2765 | 700 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 23.2967 | 24.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.186 | 42.12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.6666 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44.7 | 149 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.6 | 56 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49.8666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 73.315 | 34.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.6 | 67.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.5833 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.4667 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.55 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147.3333 | 65 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 156.6333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 169.75 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 176 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192.8667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 232.8997 | 411 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 252.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 257.8333 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 263.2 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 345.2449 | 142.86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 353.7333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 473.2 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 490 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 515.8833 | 119.05 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 550.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 560 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 590.4166 | 54.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 649.5999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 691.9 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1009.8 | 132 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1067.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1135 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1326 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1408.4333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1726.9167 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1831.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1870.6666 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2114.6666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2850 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2940 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5063.8333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7874.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49358.7666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.3332 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.4667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.567 | 51.42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.4167 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 53.6 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121.8 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 133.25 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 151 | 151 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 163 | 163 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 245.85 | 49.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245.9333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 249.9349 | 214.23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 264 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 388.75 | 311 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 499.367 | 123.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 510.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 629.9999 | 216 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 722 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1409.1665 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1534 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1861.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1941.8667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2088 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2319.0833 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2780.3333 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3006.25 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5134 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7461.9999 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21.6 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.1318 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.2 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 104.65 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 107.6667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108.3333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 115.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 165.39 | 134.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 179.6667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 246.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.2 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 256.2 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 308 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 320 | 80 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 352 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 379.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 407.55 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 490.8 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 498.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 580.55 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 591.68 | 12.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 595 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 649 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1633.6666 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3045 | 435 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3258.5 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3887 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.6 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2821.4666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 78.4 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 144 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 807.36 | 100.92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 948 | 316 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116 | 11.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 476.8 | 14.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 555.5833 | 29.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 557.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 832 | 104 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 981.3333 | 102.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.385 | 21.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195.25 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 435 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12640.7 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.1333 | 35.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94 | 47 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 131.6 | 18.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 229.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 832.4999 | 135 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1394.2833 | 37 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18.9 | 21 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 50.9667 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1428 | 204 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1927.3333 | 118 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1875.6664 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 997.5 | 525 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1102.6162 | 727 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.8333 | 0.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.4943 | 19.06 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5.85 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.4167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.0631 | 27.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.9 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.0499 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.4387 | 11.08 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.3333 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.6666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.4375 | 76.25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 86.8671 | 121.21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 99.1 | 6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 112.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.6667 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 143.4999 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 155.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 157.04 | 20.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 171 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 181 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195.45 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 198 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 201 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 212.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 246.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 259.2 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 280.3166 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 295.2 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 350.0175 | 66.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 387 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 390.8333 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 393.25 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 460 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 461.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 488.3166 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 511.8333 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 561.1166 | 128.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 576.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 659.9999 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 874 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 880 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 897.5166 | 157 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 945.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1121 | 380 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1171.75 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1363.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2281.5 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4278 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7657 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.3125 | 0.25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.6 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.2332 | 134 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.7 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.6333 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.9165 | 259 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.6 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 152.8 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 208.0332 | 158 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 212.9166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.4 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 229.1666 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270.0315 | 26.09 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 274.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 283.3332 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287.5 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 402.415 | 61.91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 554.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 640 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 677.0833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 815.3666 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1179 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2445.655 | 31.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2725.6666 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4730 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7722.9166 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31549.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.13 | 10.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 16.4233 | 37.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 72.0666 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.9833 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89.1665 | 214 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 96.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 129.6 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 131.0833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 134.4 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.25 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 208.3332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 246.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 254.1999 | 246 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 276.8333 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 287.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 324.421 | 13.17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 343 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 374 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 492 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 606.3 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 728 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 855 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1037.5 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1152 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2058 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2890.9333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9431.235 | 143.55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.3667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 149.0666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.3355 | 85.89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 511.8666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 693.45 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.8666 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.18 | 35.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.4 | 17.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.6133 | 47.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 378.25 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 758.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 150 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 350.35 | 91 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1099.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1653.6667 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.4 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.03 | 32.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 363.0167 | 23 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 256.75 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 768.9498 | 273 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 241.78 | 120.89 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 195.8832 | 161 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 211.9 | 39 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1062.7833 | 121 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1406.0833 | 47 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7056 | 196 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3183.8333 | 14 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80.8333 | 97 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1437.14 | 18.1 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19435 | 1300 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 566.6664 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 466.05 | 117 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.0353 | 41.62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.733 | 28.19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.74 | 18.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.9127 | 33.02 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.8 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.7333 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.1 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.2 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.28 | 5.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68.3333 | 205 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.97 | 14.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 98.6666 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 99.6166 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.4666 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 100.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 109.1667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.0341 | 63.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 125.8 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.25 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.6 | 329 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 156.75 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 177.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 187.2 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203.2 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 204 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211.6667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 221.2 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 224 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 234.2308 | 90.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 263.9333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 299 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 324.3 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 329.7085 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 386.3333 | 244 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 405.6 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 416 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 466.6665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 500 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 645.75 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 895.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1387.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1441 | 131 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1560 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1587.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1726.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1788 | 298 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1798.6667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2470 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3386.5 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6925.2815 | 69.87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.75 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.6 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.75 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.5 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.3 | 19.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.5333 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 184.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.75 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188.7833 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 251.9999 | 189 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 264 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 291.8833 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 333.3333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 400.015 | 114.29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 672 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 838.95 | 141 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 972 | 216 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1267.4666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1380 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3113.95 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.7467 | 8.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19.9333 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.95 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 20.2783 | 52.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.1667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 23.68 | 14.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.6 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.3768 | 187.51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.75 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.8667 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.6666 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.1333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147.364 | 66.48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.05 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 207.9 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 219 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 229.6 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.993 | 40.26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 258.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 294.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 305 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 368 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 377.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 481.8333 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 517.3666 | 166 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 524.0333 | 199 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 635.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 794.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 812.25 | 285 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 977.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1055.2667 | 44 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1170 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1264.3666 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1384.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1456.6666 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1539 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1562.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2129.4 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2328 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2762.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3243.9167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3391.5 | 646 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3546 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4290.9997 | 420 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5929.1667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41705 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.5833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 119.7 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 827.45 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 906.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.55 | 63 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.0833 | 93.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230 | 46 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.8 | 37 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1794.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.0667 | 1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.1466 | 27.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 921.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 222 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 388.9165 | 359 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 435.4166 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.25 | 5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6607.3333 | 44 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 37.6 | 48 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238.3333 | 220 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 129.1133 | 18.1 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.8517 | 10.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.52 | 8.52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.41 | 11.41 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.6667 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.4667 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.3333 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33 | 33 | 1 | 4 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.7833 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.6 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 54.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.5583 | 66.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.3667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89 | 89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 98.1666 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 109.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 161 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 161.6 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 178.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 213.18 | 61.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 221.625 | 59.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 232.375 | 27.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 232.4667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 237.9999 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 238 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 290.55 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 426.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 431.4333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 443.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 460 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 506 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 518.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 546 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 556.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 646.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 762.6666 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 768 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 849.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 882.8667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 912.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 942.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1050 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1148.3332 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1323.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1966.5333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2958.7999 | 312 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3155.49 | 89.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3225.3833 | 241 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4421.0666 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8337.5 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10630.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32312.5 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 37608 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.6666 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.0333 | 4.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.16 | 37.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.75 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.25 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.8452 | 160.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.8 | 259 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.4667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124.696 | 113.36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170.8332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 211.1515 | 29.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.3 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 304.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 494 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 748.25 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1072.9999 | 222 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1229.7999 | 156 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1472.5 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1781.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1903.0666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2137.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3837.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5504.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5722.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4.925 | 59.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.7402 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.4 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.2333 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.25 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 121.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 138.4666 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 148.8333 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.1666 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 165.55 | 8.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 193.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 200.1 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 215.3333 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 216 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 233.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 247.7999 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 250 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275.65 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 309.2833 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 323.06 | 34.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 349.2666 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 369.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 397.8 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 428.4166 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 496.6333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 557.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 581.4 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 612 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 682.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 691.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 840 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 909.9999 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 969.6 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1147.85 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1440 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1441.8833 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1738.5 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1870.9666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2340.4165 | 205 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3141.1667 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 163.2 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1588.2666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 190.6666 | 176 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 206.9166 | 124.15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 258.1 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 587.6 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.3666 | 37 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132.5832 | 185 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 153.6 | 4.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 327.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1200 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2815.8666 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.8 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 435.705 | 27.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1726.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 313.6 | 22.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 445.8667 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 506.35 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 578.7 | 54 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.15 | 111 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 283.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 559.9333 | 148 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2979.0999 | 186 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.9 | 94 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 352.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 192.4999 | 231 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 614.2497 | 405 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 655.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 766.4167 | 5 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 187.5 | 5 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 467.8666 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 66.7 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 133 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 294.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 68.75 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 427 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 405.3333 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 26.6667 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1026.7833 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 570.3333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 597.4 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1115.5333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 6447.6 | 398 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 6160 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 114.0666 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 321.7333 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 555 | 15 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1169.6666 | 121 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1436.6666 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.4 | 133 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 468 | 144 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2533.3333 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4716.6667 | 20 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 225 | 90 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 426 | 142 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1786.0998 | 318 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2028.3333 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180.9 | 54 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 829.5 | 126 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90 | 27 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 104.2333 | 13.25 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 269.3166 | 143 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 4 | 16 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 377.4666 | 152 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 423.6666 | 155 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1547.5998 | 318 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 225 | 45 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.3333 | 130 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 150 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.4666 | 152 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468.6666 | 152 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 491.4666 | 152 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1337.9999 | 90 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154 | 154 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 214.1332 | 146 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.5458 | 13.25 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.9999 | 150 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471 | 157 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3257.7083 | 47.5 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 705 | 150 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121.6333 | 82 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 401.1499 | 339 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 365 | 73 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 568 | 142 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1716 | 120 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.6666 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 308.75 | 47.5 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 362.1 | 71 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 750 | 125 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 830 | 75 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 986.15 | 121 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.3333 | 5 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 413.6666 | 73 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1468.1333 | 121 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2029.9999 | 120 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4199.9999 | 180 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1402.7 | 78 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 311.9999 | 180 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 167.2 | 88 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 453 | 151 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 554.8 | 146 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 324.3333 | 70 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 536.48 | 95.8 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 10 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 426.2166 | 107 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 626.6667 | 32 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1050 | 42 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2198.1666 | 110 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23 | 12 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 325.8332 | 170 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 696 | 80 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221.6666 | 95 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1000 | 100 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 616.25 | 87 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 809.55 | 128.5 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 872 | 80 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 549.4166 | 95 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 893.3333 | 100 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9486.8 | 24 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55.8333 | 50 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.7833 | 107 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 551.2 | 52 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.5 | 15 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312.5 | 150 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 436.6666 | 40 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 534 | 30 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.3333 | 8 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61.6 | 176 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 510.4165 | 175 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 899.3763 | 130.66 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D3-Forced - Postponed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.4167 | 5 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 364.8333 | 110 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37345 | 308 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360.9666 | 119 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520 | 40 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1462 | 68 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 20 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 32 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 410.6666 | 88 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1033.3333 | 80 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 334.5833 | 73 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 560 | 20 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.6 | 168 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 408.3333 | 100 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1316.6666 | 100 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 208.25 | 119 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 675 | 150 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D3-Forced - Postponed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 885.5 | 161 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 511.6499 | 81 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1023 | 155 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 482.9166 | 95 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.5 | 30 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.6667 | 20 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 885.4166 | 85 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159.65 | 103 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 930.6666 | 160 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.6667 | 20 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19 | 95 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 166.25 | 95 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 498.1666 | 61 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 355.2666 | 146 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270.6832 | 149 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.0826 | 68.66 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1540.5 | 45 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.6666 | 40 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 668.2666 | 28 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 36.2355 | 44.37 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 60 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 135.7 | 46 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.25 | 19 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.0833 | 95 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 912 | 380 | 1 | 1 | 0315-Pulverizer mill coal level controls | U1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.5 | 63 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.5 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45 | 45 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.3333 | 88 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.2 | 17 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105.02 | 106.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.4 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.8333 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 184.125 | 49.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 409.1333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49996.6666 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.8 | 7.6 | 2 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85.8 | 286 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.3332 | 158 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 60 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 214.2 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246.45 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.1666 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.2499 | 171 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.6665 | 232 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.5 | 194 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.5 | 234 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.9333 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.3333 | 125 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.9999 | 135 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 447.7332 | 146 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.5 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 213.6 | 17.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.2083 | 12.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 274.2267 | 13.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 325.5 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | U1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.3333 | 10 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 70 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.05 | 69 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.1999 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.7 | 98 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.1499 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.2 | 188 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.5999 | 267 | 1 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.5332 | 188 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 99.1667 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.5 | 71 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.4166 | 95 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.3333 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.05 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 301.1666 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 859.8333 | 67 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.4166 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.8415 | 16.11 | 2 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.3999 | 102 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 90 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.9667 | 41 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88 | 88 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 181.3333 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 267.7333 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 446.6 | 154 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1048.2466 | 38.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1731.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.8 | 78 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.45 | 21 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.1 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.9999 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.75 | 71 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.7 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.7 | 38 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123.5067 | 31.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.8 | 33.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.95 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.4999 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.7499 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.8 | 21 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.8331 | 287 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.8333 | 53 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266 | 152 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 564.6666 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1050.8332 | 325 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.6666 | 113 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.3333 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.8666 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 236.1332 | 161 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 389.1667 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 513 | 90 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 542.1333 | 107 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 566.1 | 54 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.35 | 63 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.8499 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26.6 | 266 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.8331 | 290 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 227.3036 | 63.73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 245.755 | 21.37 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 269.3166 | 113 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 657.3333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3362.3333 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.65 | 18.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.1466 | 26.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.6667 | 22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.085 | 23.7 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.9283 | 31.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7954 | 82 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2615.0833 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D3-Forced - Postponed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.5333 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.75 | 13 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.0667 | 19 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 893.3333 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.8333 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.3266 | 28.99 | 2 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.0166 | 59 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.3 | 54 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 359.3333 | 154 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 366.6 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 470 | 141 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.3833 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36 | 80 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.4499 | 237 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.75 | 225 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92 | 92 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 184.9333 | 38 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 216 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 500.5 | 154 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.8 | 10.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.0083 | 18.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.56 | 17.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.8333 | 53 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.6667 | 19 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.6666 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 283.9999 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 389.88 | 43.32 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 878.75 | 57 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8119 | 230 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 168.75 | 45 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 419.4167 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 659.3666 | 151 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.25 | 105 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.8333 | 53 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.9 | 63 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.3333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72.7666 | 118 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 192.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 249.1666 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 393.75 | 75 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437.1666 | 43 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 756.8332 | 239 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1395.8665 | 232 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2856 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.6 | 12 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276.74 | 41.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 570 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.28 | 16.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.495 | 15.7 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.8367 | 20.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.36 | 41.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.84 | 30.7 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 271.45 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.2667 | 2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.5533 | 16.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.3333 | 100 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.1333 | 91 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.6 | 113 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.4166 | 79 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87.9999 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1657.2333 | 166 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.6165 | 223 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.4332 | 263 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.6666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 311.4166 | 185 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.4 | 48 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.3 | 203 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.8331 | 287 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.3333 | 53 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 204 | 102 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 261.6667 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 463.25 | 85 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.0666 | 30.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 209.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 385.6 | 48.2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.6666 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.0867 | 22.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.575 | 22.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.1333 | 25.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170 | 150 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D3-Forced - Postponed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.75 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.4 | 63 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.5 | 85 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.3 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.8499 | 93 | 1 | 3 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.8 | 188 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 100 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 191.7499 | 195 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 355.2 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 830 | 150 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 931.2166 | 59 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9.3333 | 56 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.9833 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66 | 88 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.9833 | 97 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 768 | 160 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2254.2666 | 88 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.8 | 141 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29.4499 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.2 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 425.3333 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.0267 | 22.7 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.5233 | 20.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.1999 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.3333 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.75 | 47 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.4833 | 107 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.2 | 246 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.4333 | 181 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138.6666 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 174.2 | 78 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 518.95 | 97 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1016.6666 | 100 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1050.8 | 148 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1621.3666 | 127 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.6 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.6666 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95 | 19 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 173.1333 | 98 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 175.2 | 28.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.65 | 51 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.6 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.55 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135.025 | 49.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 161.7165 | 313 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 725 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 791.2 | 46 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.4 | 7.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4183.2416 | 82.7 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.7333 | 19.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105.6533 | 22.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.5367 | 30.2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 56.1 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 800-Miscellaneous
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3.1 | 6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 800-Miscellaneous
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 153.5333 | 28 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33 | 33 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 339.9999 | 150 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.66666 | 8 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.2 | 62 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2065 | 100 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.2 | 8 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 502.5 | 30 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.7999 | 96 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 428.6197 | 485.23 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.75 | 55 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16 | 8 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1076.2765 | 216.7 | 1 | 1 | 0325-Pulverizer skidding | U1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.3867 | 36.8 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 386.6667 | 50 | 1 | 1 | 0325-Pulverizer skidding | D3-Forced - Postponed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.5 | 13 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.75 | 5 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 405.8333 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 76 | 76 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.6833 | 16.6 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1507 | 60 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 82 | 82 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 522.5 | 50 | 1 | 1 | 0325-Pulverizer skidding | D3-Forced - Postponed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201 | 134 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.4 | 12 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 88 | 88 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.6667 | 10 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.3333 | 10 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.5 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.5 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 396.3666 | 94 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 509.8333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 728.75 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5226 | 67 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.75 | 3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.7333 | 13 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.0166 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 677.35 | 93 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4786.6666 | 200 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191.95 | 33 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 216 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 849.3333 | 104 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 109.8 | 54 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.75 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.3 | 29.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.3 | 34 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.7333 | 86 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129.0667 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1199.9166 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1841.6666 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 35.5 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.5 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.3333 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 607.8333 | 14 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.9 | 54 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147.3 | 49.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 216.3333 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 699.9166 | 227 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7535.79 | 114.7 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 175.2533 | 49.6 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 712.8 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 118.3333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 638.7716 | 125.66 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66.6667 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 144 | 108 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 184.1666 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 433.527 | 125.66 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3962.6666 | 160 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18303.3333 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.9166 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 307.9999 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1200.3333 | 5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 109.2833 | 79 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.4 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 243.6666 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 283.3333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300.8333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 594 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.3817 | 11.3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 183.613 | 59.23 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64 | 16 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 163.2 | 51 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 102.9 | 42 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 271.1333 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 151.2166 | 43 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.2666 | 34 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.3 | 43 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.9 | 9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111.6667 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 345.4333 | 86 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 419.25 | 39 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 492.9666 | 46 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36760 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89.1667 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329.1667 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 643.4999 | 135 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1484.1666 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.3333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.5 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.1666 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 143 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 171 | 76 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.0048 | 49.39 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 304.5 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 597.3833 | 49.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 149.6 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.85 | 27 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.9833 | 61 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.52 | 31.2 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 252.7 | 133 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 165.9 | 42 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 410.8333 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 54.9 | 54.9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320.8333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 791.8 | 214 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1967.3332 | 260 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 942 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1265.0833 | 235 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 172.8333 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 560.55 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 466.44 | 41.4 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 444.1665 | 410 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 270.9 | 54 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120.6333 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.1666 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 283.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 541.5 | 19 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 838.9333 | 52 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4756.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.6666 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 310 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1434.8 | 34 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 107.3333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 604.95 | 111 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1683.15 | 229 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 336.6 | 51 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 233.8333 | 61 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 150 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.3 | 54 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.5833 | 73 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287.1 | 99 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 408 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 525.85 | 39 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 891 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.8333 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.0833 | 91 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.6665 | 250 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1102 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 365.75 | 33 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.6 | 12 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.6667 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 166.95 | 53 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 169.2 | 54 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.7499 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 169.9466 | 63.73 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.847 | 20.67 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198.3332 | 140 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.7 | 33 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1214.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1920 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2864.5 | 102 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.0026 | 25.12 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 211.4166 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.3333 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 769.1666 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5715 | 225 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 573 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 660 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 144.0333 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 333.75 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.2333 | 14 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235.375 | 26.9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 375.6333 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 184.8667 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 687.5 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10074.6533 | 210.4 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | U2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 96.6666 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1014 | 338 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.6666 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117 | 54 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 473.3333 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1190 | 85 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.3333 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 366.6666 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 547.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42.6666 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.8333 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 144.6666 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1395 | 186 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 88.4 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1941.6666 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 137.4166 | 97 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 272 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1730.3333 | 145 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35 | 5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 64 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.3333 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 263 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 298.3333 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 446.2 | 97 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 488.25 | 93 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 960.9033 | 64.78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2337.5 | 110 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 101.3333 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 286.3466 | 47.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 497.3333 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 522.5 | 110 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 577.0833 | 125 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 823.3333 | 130 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.7 | 66 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 320.8333 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 525 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1495.8333 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2530 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 198.55 | 57 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 230 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.48 | 55.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 100 | 250 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 164.3 | 106 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 326.6666 | 49 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 554 | 277 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2875 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.25 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.6666 | 31 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213 | 142 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 217 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.25 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 288.3 | 93 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 923.3333 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1717.3333 | 184 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 538.8716 | 100.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.4 | 32.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95896.6658 | 1300 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.3666 | 94 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.2 | 24 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83.7 | 83.7 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 191.9 | 38.38 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.7107 | 43.46 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211.9673 | 20.06 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 554 | 138.5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3895 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.9999 | 150 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 414 | 92 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 468 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 745.3333 | 130 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 155 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 182.9333 | 56 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 277.5 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.76 | 11.7 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 941.4 | 54 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31 | 124 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.3333 | 86 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.5 | 38.5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 181.0666 | 56 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 261.3333 | 64 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104.65 | 23 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1674.9999 | 150 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1140 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5159.4163 | 505 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.8333 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.25 | 29.5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.3333 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 234 | 36 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 706.2055 | 46.41 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 740 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1061.6666 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1438 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.5833 | 157 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.9166 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191.25 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 349.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1235 | 130 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3009 | 177 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5219.4999 | 165 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.5 | 42 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229.625 | 50.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 269.9666 | 91 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 640 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 652.5 | 145 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 974.4667 | 47 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 261 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.184 | 34.68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 367.2 | 51 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.594 | 20.22 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1114.9999 | 150 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.5766 | 85.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 243.8333 | 110 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 444 | 148 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 957.6666 | 130 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1450 | 145 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.6333 | 26 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64 | 32 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66 | 22 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.5 | 71 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 546.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2065.9166 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12753.3332 | 400 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 75 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 301.3333 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1789.3333 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 167.5049 | 77.31 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 126.3658 | 65.93 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.5167 | 23 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 168 | 24 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 707.6333 | 142 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1127.25 | 167 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1800 | 150 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9542.6666 | 85 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.3333 | 76 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.81 | 50.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.4167 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126 | 42 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 223.575 | 48.78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 392 | 96 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 479.3333 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 767 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17 | 17 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.99 | 15.9 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 232 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 285.6533 | 41.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 334.5833 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 439.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 983.3333 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 236.6666 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 297 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2537.5 | 145 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.4 | 42 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210.8333 | 110 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.5 | 47 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 111.8 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 174.6666 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.6575 | 42.21 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 140.1666 | 145 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1777.7499 | 195 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 486.4166 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 639.9999 | 96 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 649.2163 | 60.02 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 758.3333 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 994.4999 | 270 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1241.8 | 88.7 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5389.1667 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.8333 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.5 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 952 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1171.4666 | 46 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0 | 0 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.1666 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62.3333 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 365.8666 | 56 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 415 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 462 | 88 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1469.3333 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.86 | 17.79 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.55 | 119 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 395.8333 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1037.4999 | 150 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 442.7499 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28337.1 | 554 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2165.0665 | 184 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 280 | 28 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 79.1667 | 38 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 322 | 230 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 391.5999 | 132 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.25 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85.9999 | 129 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.4 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97.5 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.9999 | 240 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 222.6666 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252.5 | 101 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 276 | 92 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 311.6666 | 34 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 341.9999 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 908.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 204 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 278.01 | 92.67 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.4167 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 607.86 | 101.31 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187.6917 | 22.3 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76.4166 | 131 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 603 | 201 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 468 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.9493 | 51.32 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.4 | 57 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.3 | 6 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.3333 | 8 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 232.9 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 594.3 | 63 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 749.9999 | 180 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1065.75 | 152.25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1752 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.1667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 548.3332 | 140 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 662.4999 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6572 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8 | 10 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.9 | 54 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134.1667 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 478.3333 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 552 | 138 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 728.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1657.5 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2760 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16.25 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.8 | 9.6 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 10 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 143.5933 | 18.1 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13399.9998 | 600 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 411.4 | 44 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 448.4999 | 207 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 623.3333 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 728.5 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.6666 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 549.9999 | 132 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 607.7498 | 280.5 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 936.8275 | 55.93 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1043.1666 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33.6 | 168 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92.0833 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252.8 | 48 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 566.4999 | 165 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 825 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3108.3999 | 228 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 432.68 | 37.3 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.3333 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150.5 | 14 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.1666 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 245 | 140 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 363.35 | 169 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 640 | 160 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 751.6665 | 205 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.5 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.0666 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155 | 124 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 201.5833 | 205 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 380.8 | 84 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 483.7666 | 46 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32.4999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55 | 10 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135.3333 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 411.6 | 84 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 511.3333 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 633.1666 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 280 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 287.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 215.3333 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 286 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.8 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.65 | 117 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320.8333 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 779.1666 | 275 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1248.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1500.8 | 32 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2351.1499 | 177 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 4662.1013 | 491.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.8332 | 155 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.9166 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 736.3333 | 235 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1702.0832 | 215 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 504.3999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 236.55 | 57 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204.4166 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288.9333 | 44 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 352.8 | 126 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.9 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.2666 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.9333 | 31 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 181.2 | 72 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 125 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 272.85 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 594 | 36 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 7.4293 | 27.86 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 376.8333 | 119 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1011.3332 | 164 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 316.6666 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 187.0666 | 46 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246.5 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 920.7 | 51.15 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.8333 | 10 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61.8666 | 116 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 103.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456.9333 | 184 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 718.6667 | 14 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 943.3332 | 200 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4584 | 160 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.9999 | 210 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 534.4166 | 121 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 550 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.5333 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 52.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 138.6 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153.0833 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 214.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 592 | 111 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 745 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 749.7 | 119 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 234 | 117 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 138 | 69 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.1667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.0667 | 22.6 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.0333 | 62 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 59.5833 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.3333 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 441.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2100 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 38.7034 | 211.11 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171.55 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 299 | 74.75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 636.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.8333 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1353 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 320 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1074 | 134.25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 210 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2.75 | 11 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 143.3333 | 43 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1523.4569 | 242.46 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 232.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 341.9166 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.6666 | 130 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175.5 | 90 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 113.75 | 65 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 81.9836 | 104.66 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8336.6663 | 610 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1532.4665 | 181 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50 | 50 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.9999 | 153 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 541.3333 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1449 | 15 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 157.6666 | 172 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 212.5 | 15 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4282.5 | 45 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.3333 | 10 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.3333 | 62 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.8 | 31 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64.1667 | 50 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.5 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 118.9215 | 88.09 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.5 | 45 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1403.4665 | 304 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 309.8666 | 112 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 820.8333 | 250 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.3 | 26 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.9666 | 65.95 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.8333 | 70 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 301.5833 | 55 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 88 | 160 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.75 | 84.5 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.9166 | 155 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 155.3666 | 118 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 485.3332 | 140 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.1666 | 74 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193 | 96.5 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 210 | 140 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 308 | 140 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2206 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 230 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 314.7167 | 23 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 927.5 | 35 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 263.9999 | 180 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65 | 78 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4120.0666 | 92 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.85 | 16.2 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 190 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 455.3333 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.8333 | 70 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.9 | 62 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.3333 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 133.965 | 68.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 293.3333 | 110 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 360 | 160 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 595 | 102 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1793.9999 | 180 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81 | 81 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 237 | 45 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.6667 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 460 | 50 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.3 | 69.3 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.1666 | 70 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.2 | 42 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 210 | 210 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437.5 | 75 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.5999 | 78 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.75 | 121 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 253.5833 | 85 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 280.25 | 95 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.2 | 19.8 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.5833 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54.9999 | 150 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56 | 160 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 207 | 138 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 222 | 185 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 263.9999 | 360 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 356.6667 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D3-Forced - Postponed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 344.4 | 28 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 650-Fluidized Bed
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 16.2 | 18 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 650-Fluidized Bed
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 34.5333 | 28 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 650-Fluidized Bed
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6765.0666 | 92 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58529.6665 | 530 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 601.8333 | 62.8 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 825 | 30 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5745.4 | 92 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6120.4 | 52 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1226.2667 | 8 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3143.3333 | 92 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 153 | 102 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 182.85 | 23 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 450.6666 | 80 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125.8346 | 80.32 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.175 | 26.7 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24895.1999 | 414 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70447.0829 | 575 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 299.5666 | 43 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 351.1666 | 70 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 343.65 | 17.4 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.4247 | 34.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.3333 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.654 | 396.54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.5 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.9907 | 17.14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.8666 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 60.9 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.6666 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118 | 40 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.1666 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160.65 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186.6667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 199.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 201.25 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 218.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 256.5 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 269.5 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.6666 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 322 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 322.6666 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 324 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 336.85 | 3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 367.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 390 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 400.5833 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 404.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 411.1566 | 184.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 575.1 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 600 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 620.5 | 3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 637.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 701.6 | 87.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 896.9999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 980.8333 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1072.5 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1967.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2407.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3487.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7821.9165 | 265 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.4166 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.4999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41 | 41 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.3 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.4166 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.0833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 165 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.5 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 231.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232.9 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266.75 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 327.7 | 113 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 342.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 349.0665 | 187 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 365 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 493.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 708.4425 | 48.03 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 826.42 | 59.03 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1050.8266 | 129.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1184.6499 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1539.1666 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2232.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8538 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.3333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.1333 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 85.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.4333 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.297 | 220.66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 164.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 172.3332 | 188 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 182.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 212.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 227.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 256.6665 | 280 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 315.1333 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 369.9908 | 108.29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 396.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 433.3333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 448.699 | 133.94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 474.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 561.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 650 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 773.4999 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1050 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1396.8 | 288 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1595 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1635 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1940.8332 | 274 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2264.9999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6786.4166 | 185 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7300.8 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7445.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11230 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71 | 35.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 133.42 | 66.71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 54 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1103 | 110.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224.875 | 128.5 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3954.7666 | 119 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.3416 | 45.1 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 622.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2640 | 10 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.61 | 26.87 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 735 | 28 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25550.4166 | 65 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.8933 | 21.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.9 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.0833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 70.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.3333 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.5 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.25 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.3333 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 229.1666 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280.5833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 317.3332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 424.3332 | 318.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 453.75 | 99 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 535.1666 | 169 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 610.2 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 782 | 184 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 834.2583 | 104.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 872.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 894 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 925.7975 | 27.35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 927.0833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1075.0833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1100 | 275 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1885.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3806.25 | 375 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13474.8 | 342 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0 | 0 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.4333 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.9333 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.5 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103.5265 | 80.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 124 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.0833 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 141.5553 | 10.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 157.4999 | 135 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240.7999 | 84 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 274.2667 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 281.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 313.75 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 314.5833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 331.25 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 403 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 685 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 700.8 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 925.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 930.75 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 998.7498 | 255 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1033.5 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1076.65 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2006.6666 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3269 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11914 | 185 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.8167 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.5 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.8333 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108.3333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 197.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 231 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 283.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 367.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 412.0833 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 461.5 | 130 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 470.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 577.5 | 210 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 644 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 841.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 980 | 245 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1093.6666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1367.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1419 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1814.5832 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1819.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2953.1666 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3477 | 183 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4004.1 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4830.8333 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4918.0265 | 45.03 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5717.7 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 313.6 | 78.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.0012 | 10.19 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.4433 | 32.9 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38279.5833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 725 | 60 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 940 | 235 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1377 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1819 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2929.6664 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3247 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.35 | 43 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130.5 | 104.4 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 131.2666 | 179 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 310.3331 | 380 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 464.5833 | 223 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 16 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.6666 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.2292 | 34.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.65 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 83.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.5833 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.6667 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.9666 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137.75 | 71.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 146.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 153.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.25 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 166.25 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 171 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 172.8816 | 110.35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 213.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 214.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 217.9167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 232.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 245.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262.5 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 294.3233 | 160.54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318.0833 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 339.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 340 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 346.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 376.25 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 379.1665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 390 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 414.7283 | 160.54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 444.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 512.5333 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 516.25 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 519.7499 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 545.3 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 555 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 603.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 649.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 697.6666 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 870.8333 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 932.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1002.7499 | 157.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1086.5833 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1123.85 | 247 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1132.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1252.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2730 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3654.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4904.4 | 134 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10224 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.1333 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.6 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.0667 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 49.25 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85.8333 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110.4167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.8333 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 153 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 216 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 295 | 59 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 308 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 309.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 320.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 419.25 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 444.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 594.6525 | 111.15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 683.8333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 689.4 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 705.6666 | 116 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 737.3333 | 112 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 897.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1045.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1080.2333 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1527.1666 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1729.8333 | 107 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2136.75 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2214.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2552.4 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3209.5999 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9794.1333 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.96667 | 1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.0333 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.55 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.6099 | 105.66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39 | 19.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 40.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57.5 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 202.6666 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 212.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 233.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 265.0433 | 51.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 283.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 297.85 | 51.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 307.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 345.8333 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 387.6 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 394.3333 | 130 | 1 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 582.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 780 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1227.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1400.5333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1991.4 | 3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2647.2 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3028 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3863.7 | 159 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 875.38 | 79.58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2330.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 124.55 | 47 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 349.6 | 15.2 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9844.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10036 | 65 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456.95 | 48.1 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 892.5 | 85 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2244 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 487.6665 | 380 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9390 | 600 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.8171 | 24.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.6666 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.1667 | 1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.5 | 190 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 141.25 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160.4167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.75 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.3331 | 290 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.44 | 32.24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 213.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 232.3 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 277.0833 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 287.5 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 290.16 | 32.24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 327.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 342.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 357.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 376.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 531.6665 | 220 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 545 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 758.9999 | 198 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 844 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 927.4166 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1000 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1031.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1626.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1733.53 | 68.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1766.1 | 174 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1862 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2248.022 | 65.54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2701.45 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3095.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45517.5 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55029.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.6667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.5833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.0667 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.5 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.0833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 146.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 197.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 416 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 434.5833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 507 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 614 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 639.24 | 53.27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 706 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 789.5833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 826.8666 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1806.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3676.6667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.7333 | 16 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.6666 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62.3332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 80 | 32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84 | 84 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 88.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 95 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 98 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 130.0693 | 75.04 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 178.5 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 183.1667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 370.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 384 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 433.5 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 435.4166 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 475 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 525 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 608.75 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 661.689 | 81.69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 728 | 91 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 765 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 770 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 820.1666 | 51.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2252.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 802.0833 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.67 | 41.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 115 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.04 | 22.6 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.5 | 13 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.0407 | 16.04 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1963.59 | 17.4 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 144.3849 | 129.3 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 388.3664 | 382 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.8466 | 36.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.1666 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.2333 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 139.15 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.75 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 162.7576 | 65.54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 179 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 188 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209.0666 | 44.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 272.48 | 62.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 279.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 299 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 326.875 | 261.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 347.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 472.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 488.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 494 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 525 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 708.5 | 109 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 754 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 766.5 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 788.5 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 885.5 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 979.94 | 75.38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1120.8332 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1168 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1354.1665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1538.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1652.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1704.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.95 | 47 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.9 | 42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55.9708 | 95.95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 149.4 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.75 | 89 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 222 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240.8332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 248 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 260.4 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 373.1 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 402.0833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 434.6666 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 472.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 512.4 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 612 | 272 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 643.4333 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 675.75 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1108.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1185.9666 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1338.6 | 69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4042 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4057.0833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4127.4666 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.7 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42.3 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 81.7868 | 63.73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132.9166 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.8333 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.5 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 405 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 425 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 452.8333 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 457.5 | 45 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 492.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 500 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 528 | 320 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 530.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 551.7 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 570 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 673.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 758.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 790.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 807 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 870.8333 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1449.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1768 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2146.6666 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2207.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3376.4995 | 44.99 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 269.71 | 269.71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 315.99 | 105.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 417.33 | 139.11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 87 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.4166 | 95 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.395 | 20.3 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.8083 | 22.9 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 234.5 | 100.5 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1146.1667 | 23 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.2182 | 16.57 | 2 | 2 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24.5 | 105 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.6666 | 52 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 234.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1017.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1690.5 | 16.1 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1399.6664 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 553.9 | 382 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.5 | 2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.5 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.0333 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.0075 | 34.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.4667 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.1875 | 95.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.6666 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 118.5 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 134.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155.2833 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 173.3333 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 188.5 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 255 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 270 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 338 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 475.695 | 96.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 616 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 622.4999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 683.7666 | 146 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 729.35 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 751.8623 | 160.54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 834.1667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 843.9998 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 890 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1055.8416 | 128.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1137.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1395 | 225 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3037.5 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3456 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.35 | 41 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.8166 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.5 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.192 | 135.48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.15 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 142.8 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 190.8 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 299 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 337.2916 | 161.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 416.4333 | 96.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 438.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 445.2 | 42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 506.25 | 225 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 507.6 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 516.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 559.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 670.2667 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1235.25 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2080 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3496.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2.9167 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.5667 | 8.56 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 69 | 69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.25 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89.9999 | 270 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 125.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 163.7999 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 209 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 258 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 262.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 297.6667 | 47 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 387.3333 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 399.3 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 539.5 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 544.6665 | 190 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 567.3333 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 573.9999 | 210 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 615 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 652.05 | 69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 708.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 766.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 795.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1066 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1407.6 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1699.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1722 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2496.8667 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3815.5333 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4998.6 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42840.4166 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.02 | 27.02 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 275 | 68.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 441.15 | 88.23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 347.9166 | 125 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 475.3166 | 79 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1363.25 | 109.06 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.1667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.8 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.61 | 25.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.9333 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.3333 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 87.6667 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.5833 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.0666 | 49 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.8667 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.3333 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 237.3 | 113 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.8333 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 256.1166 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 266.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 289.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 294.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300.3333 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330.4166 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 381.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 425 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 452.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 473 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 494 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 540 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 552.5 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 662.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 696.5 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 962.5 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1004.1667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1050 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1656.25 | 265 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3577 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10175 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.9 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.85 | 3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 83.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 94.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 200.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 242.1 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 303.8 | 217 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 364.8666 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 383.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 405.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 420.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 453.1667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 489.6 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 496.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 722.9167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 731.5 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 747.6 | 84 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 870.7499 | 243 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 898.8666 | 194 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1081.7333 | 76 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1230 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1410.5 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2100 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2254.5833 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2962.4999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3784 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3842.16 | 12.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.8333 | 22.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.6666 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.4332 | 146 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91 | 91 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 101.4999 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 108 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 173.25 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 177.25 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 184.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.5833 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.8332 | 215 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 267.75 | 153 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 285 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 321.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 331.2 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 356.5 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 370 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 412.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 426.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 581.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 657.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 687.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 699.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 760.0315 | 119.69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 765 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 918.8333 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 999.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1008.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1045 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1061.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1180 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1180.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1303.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1419.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1805.05 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2253.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2583.9 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3265 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7819.7333 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 724.98 | 120.83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134.2667 | 15.2 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 562.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23486.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2016.3667 | 48.2 | 1 | 1 | 0340-Other pulverizer problems | U3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.4999 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35.8 | 3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.9349 | 105.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.2499 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.9667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 126 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 137.75 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 144 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 162 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 185.65 | 47 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 192.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 281.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 322.5 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 361 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 377.5 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 664.1667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 691 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 750 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 888.3 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1078.3667 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1156.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1292.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2781.6 | 114 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3054.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3597.4999 | 150 | 1 | 3 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.8833 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.6667 | 16 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.4333 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.3333 | 32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 176.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 187.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 204.1666 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 251.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 267.6666 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272.85 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 300 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 304 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 411.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 431.2 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 498.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 558.3333 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 758.3333 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 907.1 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 931.2332 | 307 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1115.5666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1188 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1752.5666 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2028.6 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4434.1666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16818.1833 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.25 | 3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.6 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 82.9165 | 199 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.5 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 170 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 236.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 249 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 282 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 305.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 337.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 416.5 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 428.75 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 847.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 960.5 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1653.75 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2058.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2247.5 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3187.5 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 296.7 | 98.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 566.04 | 47.17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 139 | 69.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 807 | 80.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158 | 79 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1120 | 160 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 601 | 60 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4283.75 | 575 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4544.6664 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 356.8 | 223 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 216 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 286 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 833.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 590 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 75 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 726.4 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 58 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 149.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 246.4 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 23.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 21.5 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 464 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 866.2666 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3.5 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 800-Miscellaneous
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 0.18333 | 1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 800-Miscellaneous
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2715.1666 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 497.4833 | 19 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1510.1665 | 410 | 1 | 1 | 0341-Pulverizer deluge system | U1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1166.6666 | 70 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.5 | 50 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 502.8333 | 70 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 323.42 | 161.71 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7223.3333 | 100 | 1 | 1 | 0342-Pulverizer inert system | U1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 545.073 | 117.22 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56.8333 | 55 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1364.2442 | 126.71 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4166.9832 | 133.7 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 571.6666 | 70 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1551.3333 | 65 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 102.6666 | 140 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 633.55 | 126.71 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.0166 | 73 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 351.61 | 50.23 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 761.25 | 50.75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1004.5 | 14 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.8499 | 123 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 653.3333 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 248 | 62 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 281.6666 | 65 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1050.3333 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4496.3333 | 70 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 225 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1355.9005 | 80.31 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2438.6666 | 124 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7362.0998 | 249 | 1 | 1 | 0344-Pulverizer inspection | SF-Startup Failure | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.25 | 63 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107 | 107 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 164.25 | 36.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 720 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1024.0333 | 31 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2626 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5867.3333 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9 | 108 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 77.5 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.6 | 68 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 294.15 | 53 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 302.8333 | 46 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 607.0666 | 58 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 888.125 | 122.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 888.3333 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 272.1666 | 115 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 607.55 | 87 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1908.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238.3333 | 55 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.7333 | 77 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.9 | 46 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 634.8333 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4599.1 | 55.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.5 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 441.45 | 9 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 505.9999 | 120 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 592.6666 | 140 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.8 | 9 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109.3333 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130.3333 | 46 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 851.5 | 131 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2398.6999 | 102 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.3333 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.25 | 25 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 265.4166 | 91 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2515.5 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.5 | 23 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1284.1666 | 115 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1949.7499 | 165 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5292.9333 | 214 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468 | 120 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 873.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1441.7 | 78 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104.9667 | 47 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 612.8999 | 81 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1960.4166 | 125 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.5 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 780.8333 | 25 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1235.25 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 25.3333 | 38 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.5333 | 53 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 264.4166 | 95 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 311.6666 | 55 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 718.75 | 75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 902.1 | 93 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2092.5 | 270 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 192 | 8 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340.6666 | 40 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 109.6666 | 28 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128 | 128 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.5833 | 74.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 194.0833 | 85 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1477 | 14 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.6667 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.2 | 64 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210.4167 | 25 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228.75 | 75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1031 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145.5 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.6667 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2948 | 110 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 421.6 | 124 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 404.7 | 114 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1429.6333 | 77 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82.8 | 46 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 600.6666 | 40 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1177.5 | 150 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 466.6666 | 40 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53 | 53 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80.475 | 55.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.3333 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 294.1167 | 7 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 539.3333 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 826.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 843.5 | 35 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.9999 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 148.3333 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 412.5 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 211.5 | 70.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.65 | 29.5 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 390 | 150 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 295.2 | 123 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 377.0833 | 125 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 243.4666 | 88 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1316.6999 | 189 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3558.3333 | 122 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 108 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.6666 | 64 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.5 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 401.9166 | 91 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 553.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1609.5 | 55.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7213.5 | 21 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65 | 13 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 272 | 136 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 406 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 578.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.823 | 7.87 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.7 | 38 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 407 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 218.01 | 72.67 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42.12 | 21.6 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 434.25 | 193 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15 | 25 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.6667 | 10 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 10 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1533.3332 | 200 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4998 | 120 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 805 | 35 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.1667 | 5 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 782 | 17 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1294.0833 | 53 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1700 | 85 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3834.7666 | 58 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1962.6 | 36 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.6 | 2.6 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2011.15 | 29 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 274.5333 | 58 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43377.5833 | 55 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 750 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 305 | 100 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 853.1833 | 7 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2318 | 61 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1735 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5064 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94.5 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 679.4 | 34.4 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2942.5333 | 58 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5820.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.2 | 3 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 875 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2277.5 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2495.8333 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4536 | 84 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7789.3999 | 102 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32001.9333 | 187 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 269.25 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272.7666 | 98 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 565.8333 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1844.595 | 22.9 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11136 | 58 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.9166 | 55 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1536.6 | 36 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1732.8 | 36 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6586.2117 | 16.9 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 457.2917 | 2.5 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 857.5 | 70 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 957 | 116 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1743.3333 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3051.0333 | 53 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13006.1332 | 272 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2698.9333 | 58 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6380 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 389.31 | 34.2 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 849.5217 | 13.9 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1155 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8745.8333 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 947.25 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 641.275 | 22.7 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 713 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 877.25 | 33 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1384.9333 | 13.6 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2484.65 | 31 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2764.6666 | 104 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 599.1333 | 43 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 808 | 101 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 973 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1427.9166 | 25 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2265 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1995.8333 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 409.6 | 12.8 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 638 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1398.475 | 16.9 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8866.6666 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10012.3333 | 28 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 384.2 | 113 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.8333 | 34.7 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.6666 | 100 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.1667 | 14 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5460.8 | 48 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 767 | 118 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5655 | 60 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 305.2233 | 12.7 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14170.65 | 507 | 1 | 1 | 0345-Pulverizer overhaul | U1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 685.0153 | 12.82 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 740.3166 | 43 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 765.75 | 9 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24 | 36 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 715 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2447.8167 | 22.7 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19927.5533 | 66.8 | 1 | 1 | 0345-Pulverizer overhaul | U1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.7463 | 23.54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.1667 | 22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468.2999 | 126 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 701.6666 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 838.3 | 166 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220.9999 | 102 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.3333 | 22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141.75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 287.8333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 363 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1521.3333 | 163 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1799.0666 | 131 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.55 | 31.4 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.1667 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.5833 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.5833 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 96.8 | 176 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 172.3165 | 211 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 935.7332 | 176 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1616.2666 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4.4333 | 14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13.75 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 53.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78.6666 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 132.9999 | 105 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 164.6999 | 162 | 2 | 2 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 185.25 | 195 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250.25 | 105 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 234.6 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 32 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27 | 18 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.4666 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206.6666 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 281.2 | 148 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 481.0667 | 22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 510 | 102 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 633.1665 | 262 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.9 | 67.25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 283.2 | 96 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51.3333 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.3333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.6 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 70.8333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 246.75 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.8 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48.5333 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 62.8666 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.45 | 147 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 576.1999 | 129 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 74.2 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 127.5 | 255 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 137.6666 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 562.9165 | 193 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7122.5 | 185 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 292 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 380.2666 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.8 | 12 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1084.1666 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.8 | 12 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.6667 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170 | 85 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 262.5 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 305.25 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 501.3333 | 94 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 544.1833 | 103 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 566.25 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4294.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.9176 | 139.42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 814.9333 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 817.3875 | 46.05 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3.6 | 12 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.15 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.7499 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.4 | 72 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.2 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40 | 32 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.7 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.1166 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.3332 | 170 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 152.1333 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 156.9333 | 88 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 180.8333 | 175 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 191.7499 | 195 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 192 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1241 | 170 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4061.8666 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.1 | 66 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.2 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 170.6666 | 160 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 218.1833 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 11.25 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.6666 | 200 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.25 | 197 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.45 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 75.05 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.1 | 18 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.3333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.8 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83.95 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 200 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 229.5833 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 696.6666 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 759.9999 | 114 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1212 | 101 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.7811 | 66.67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.3333 | 92 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147 | 98 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 206.6666 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 18.5985 | 41.33 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.5 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 241.5 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 245.1997 | 151.67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 434.75 | 185 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 931.6666 | 86 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1541.6666 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 494.6666 | 106 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.75 | 27 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.3333 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51.7 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.35 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66.2666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.3333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.1 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 97.5 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 133.3332 | 125 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138.55 | 163 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 139.3333 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 192.05 | 69 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 354 | 177 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.85 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.4 | 76 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 69.6 | 144 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 76 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 122 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 165.6 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63.5833 | 109 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.35 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.15 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.4166 | 185 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 90.6666 | 160 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 114.4665 | 202 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 132 | 132 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 475.85 | 307 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 964 | 241 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240.2666 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 416.4166 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.784 | 49.44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.118 | 71.67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632.5 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72.25 | 17 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.6667 | 10 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.238 | 75.17 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 453.75 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.2 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.9333 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 50.35 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.8 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.4 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.85 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 119.9666 | 118 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 134.3666 | 139 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 164.8332 | 215 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 179 | 179 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 69.6 | 29 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 102.6666 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 83.85 | 43 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 105 | 175 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 145.8333 | 175 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 232 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 278.6665 | 220 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 541.75 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 655.4166 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89.4833 | 91 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106.25 | 85 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.95 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.8841 | 135.35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.25 | 40.1 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.1167 | 41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 253.3333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 257.1333 | 66.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.4366 | 29.8 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.92 | 34.8 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 127.5 | 170 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.7 | 37 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.7833 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.25 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 115.8 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 900.9999 | 159 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1201.0833 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.5667 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67.8 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.4999 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 187.5 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 526.0332 | 367 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.4666 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.75 | 185 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 157.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 178.7499 | 195 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 394.3332 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 435.5332 | 188 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.6667 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.3333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.8666 | 37 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 655.1999 | 216 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2557.3332 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.6666 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.9 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110.8333 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 272.55 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 928 | 128 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1295 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.5 | 34 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.14 | 30.6 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.4 | 12 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.1 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.6333 | 22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.9333 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.2 | 43 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.9166 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 202.5 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 223.2 | 186 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 284.1999 | 174 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9502.2333 | 178 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.6 | 21 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.8332 | 170 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120 | 72 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.5 | 130 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 53.9 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 55.35 | 41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.5 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 119.9998 | 288 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 169.1333 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 175 | 175 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 307.1667 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 316.2499 | 165 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 660 | 200 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 345 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 530.1 | 93 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 252.6667 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 686.5332 | 271 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.2499 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110.4999 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 317.25 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 642.5 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 840.2333 | 91 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 227.7333 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.995 | 24.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 370.5 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1076.9 | 121 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1408 | 220 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.9733 | 23.6 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.6666 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.85 | 33 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54.75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.8 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 93.3333 | 175 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 154.1 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 167.1999 | 132 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 228 | 190 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.5333 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.75 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 160.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26.2498 | 225 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 103.4 | 94 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 212.7999 | 228 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 12 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.7333 | 11 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.8 | 4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.9 | 87 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81 | 9 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.5 | 6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.0832 | 143 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 206.8332 | 170 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 348.5 | 41 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 368.6666 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1126.2333 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4301.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.8333 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.3333 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1713.8832 | 263 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1995 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3820 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10203.2666 | 61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.4 | 82 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 112.4166 | 71 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 125 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 138.6 | 198 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141.55 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 267.1666 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1756.8953 | 138.52 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 57.5 | 69 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72 | 72 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 308.805 | 72.66 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 655.05 | 43.67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 239 | 59.75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 380.01 | 126.67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.915 | 21.3 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.75 | 22.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 246.1333 | 104 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.8333 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.5 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.6665 | 250 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 113.1666 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192.5 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 421.07 | 64.78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 430.5 | 41 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 447.0833 | 145 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 767 | 52 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.25 | 97 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.5 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 504.1167 | 29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 582.6666 | 92 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1804.8333 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5830.5 | 130 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49.5999 | 96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123.3413 | 40.22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 272.4666 | 61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 308.75 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.84 | 17.8 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.5333 | 38 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.9167 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 902 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6022.8 | 252 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1094.1666 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.1 | 33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18 | 18 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.45 | 33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.5 | 42 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187.2 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 393.3333 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 659.2666 | 62 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4306.6664 | 340 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5800 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6446.9999 | 180 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 131.655 | 60.3 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.9166 | 53 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 231.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 466.6 | 3 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 691.25 | 105 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 703.0833 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1014.3332 | 340 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1032.5 | 105 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2323.3332 | 340 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3274.5 | 118 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4094.75 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.3333 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 137.8667 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 418.3333 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 281 | 56.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 701.76 | 87.72 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2149.28 | 113.12 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 496.11 | 129.42 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 252.8 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.6667 | 38 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.9333 | 56 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 401.5 | 146 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2307.4997 | 390 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.3333 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111.1 | 101 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127.4998 | 225 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 134.1666 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 151.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 346.1666 | 67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 379.1667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 467.5 | 102 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 479.6667 | 20 | 1 | 2 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 532.9999 | 195 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 662.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 846 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.8999 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.3 | 39 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 268 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 630 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1076.5 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10369.3333 | 77 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 226.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 80.0833 | 31 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 511 | 146 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.65 | 21 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.1 | 33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121.8 | 84 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132.1299 | 108.6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210.2499 | 87 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 216 | 96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 399.4667 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 436.6 | 111 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 959.5832 | 245 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1662.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.3333 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.75 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.5 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.4 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180.8333 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 219.1667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228.8999 | 126 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 246.25 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 279.5833 | 61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 399.0833 | 5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10197.1666 | 61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62.3333 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 180 | 240 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1348.6666 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1634.8 | 268 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.2833 | 61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.4833 | 24.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1584 | 160 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.3333 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 14 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.1475 | 73.53 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.75 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.1666 | 95 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.45 | 10.6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209.2666 | 43 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 225 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 434.9999 | 180 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1243.9999 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107.7333 | 64 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 195 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 247.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260.7998 | 489 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 583.5 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1047.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2083.4166 | 115 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2100 | 112 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2206 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2340 | 260 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2909.5833 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 274.1667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 678 | 113 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1366.205 | 160.73 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 203 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 236.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1696.5 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.3333 | 68 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.7333 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.8333 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132.05 | 57 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 146.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165.3666 | 82 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 72 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 235.9999 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 338.3333 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 383.5666 | 74 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 828 | 72 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1361.6665 | 190 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.3333 | 5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.8333 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250.3333 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 293.75 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385.9999 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1759.0664 | 334 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4409.1666 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4641 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.2 | 108 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 157.5 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1764.5832 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 65 | 13 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 376 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5310.9735 | 85.73 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.8833 | 39.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 420.5667 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29249.75 | 395 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.6666 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.6666 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.1666 | 67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 166.8333 | 130 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180.6667 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 250 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 392 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 677.3333 | 160 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.4167 | 5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.9545 | 43.67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.6666 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 247.5 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 599.9 | 3 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 963.2 | 64 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1621.5 | 47 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2451.25 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2494.9 | 61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4384.5 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7974.1165 | 193 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12580 | 170 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 246.5 | 170 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 445.8999 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 481.75 | 47 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 745.3666 | 118 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1033.3332 | 200 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1086.2715 | 40.01 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1560.1666 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 498.1 | 99.62 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 413.95 | 82.79 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 668.22 | 111.37 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.5333 | 25.6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 141.1667 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 124.5 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 469.6 | 24 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 17.5 | 15 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 1036 | 148 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 22.9167 | 25 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 95 | 190 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1740.1328 | 842 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.6 | 82 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.75 | 75 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2107 | 147 | 1 | 1 | 0358-Oil burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2468.3333 | 50 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3966.6663 | 595 | 1 | 1 | 0358-Oil burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 256.6666 | 100 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.6333 | 29 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.7833 | 19 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1157.5 | 50 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 120.8333 | 250 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 382.6665 | 280 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 39.5 | 79 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 728.205 | 112.9 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52.5 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 188.0833 | 61 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57.0667 | 32 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 301.3333 | 160 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2119.513 | 434.03 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 663.3333 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 313.9999 | 120 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 410.25 | 547 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 883.5 | 19 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 27.9999 | 336 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 20.4 | 20.4 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 10.1333 | 32 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 679.35 | 647 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1075.8 | 132 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 52 | 130 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 573.3 | 573.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 288.1645 | 134.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 722.3333 | 110 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 689.9999 | 450 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 285 | 300 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 372 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 931 | 665 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 247.2833 | 37 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1579.5285 | 99.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 56.5333 | 106 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4732 | 65 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 10.8 | 36 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 108 | 240 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 198 | 180 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 89.3331 | 335 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1170.4 | 48 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 506.3332 | 155 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1702.4998 | 450 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 86.3999 | 81 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 115.9999 | 240 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 409.01 | 584.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 457.3 | 457.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 147.682 | 54.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 416.8173 | 44.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 431.415 | 287.61 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2861.2162 | 44.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 708.75 | 675 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1348.5 | 90 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5896.8 | 81 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49.5 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 172.0833 | 35 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 0 | 0 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0 | 0 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 17 | 34 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 149.4166 | 55 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 165.8666 | 311 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5268.7999 | 222 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.1333 | 58 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 95.6666 | 140 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 365.4998 | 258 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1789.0331 | 562 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 68.1333 | 28 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 310.8 | 111 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 6459.1499 | 153 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 70 | 28 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 64.8666 | 28 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 279.3 | 114 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 123.5 | 114 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 14 | 28 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 342.25 | 111 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 554.7665 | 178 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 189.9333 | 77 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1450 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 313.7833 | 67 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 122.5 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 39.05 | 33 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 295.5 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1073.7 | 54 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 0 | 0 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Winter | 464.3832 | 149 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2014 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 47.4 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 34.6666 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 332.5 | 75 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 157.6666 | 110 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 338.8333 | 95 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.9166 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2949.1166 | 67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2990.65 | 111.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.4999 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.75 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.0833 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 166.5 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320.1666 | 170 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.25 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.4 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62.8833 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.35 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 116 | 87 | 1 | 2 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 169.5999 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.0999 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.8 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 283.5 | 189 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 339.5 | 97 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 501.6999 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1080 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 332 | 332 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 930 | 12.4 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8165.6333 | 199 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1197 | 630 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.7 | 74 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 174 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56 | 56 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 321.763 | 20.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 362.6666 | 170 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 725.1666 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.4166 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.0166 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.2 | 63 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 301.4133 | 101.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.8117 | 17.9 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 167.2285 | 115.33 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1540 | 28 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.54 | 17.4 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6543.6832 | 197 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5594.9999 | 450 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77.9999 | 117 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 60 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3207.4666 | 97 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.0666 | 76 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.2666 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.9999 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80.2333 | 83 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130 | 130 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190.95 | 67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 337.2849 | 155.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1917.25 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 133.2 | 74 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 519.5832 | 215 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 811.2975 | 20.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.85 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 594 | 88 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.2 | 3.4 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.6 | 7.3 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 871.8165 | 181 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.5833 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.3999 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1010 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1742 | 67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3418.1166 | 67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12808.1666 | 67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105075 | 150 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.4999 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 319.25 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 466.0833 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 469.9999 | 120 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 525.4166 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 649.9999 | 120 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1334.0833 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.7666 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.25 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125.5 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156.8 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 401.2165 | 181 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 440 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 184.5749 | 96.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.45 | 51 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.4666 | 52 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.8333 | 91 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 398.95 | 79.79 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 402.6 | 66 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1245 | 150 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.8 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.3833 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 104.3835 | 20.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108.3333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.3333 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1830.3331 | 380 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.35 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 561 | 187 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18580.6667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.8733 | 16.4 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.78 | 29.4 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 222.3 | 117 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32088 | 191 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.5 | 83 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.1666 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132.5666 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 323.4 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 517.5 | 150 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 637.5 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 827.7499 | 129 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.0333 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.2667 | 32 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261.4755 | 20.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 150 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15283.3333 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.1333 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.4166 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90.4666 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 490 | 175 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1159 | 244 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 10095.8 | 22 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.88 | 26.4 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.4933 | 44.8 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1017.1 | 14 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 100 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 255.45 | 393 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 153 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 336.1249 | 80.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 347.4999 | 150 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 538.9358 | 174.79 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 665.2166 | 167 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8050 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.8267 | 19.84 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98.1666 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160 | 120 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 297.6666 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 667.8167 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1287.5 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8725.3331 | 320 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15438.3333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 134.4 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 168.6665 | 184 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13383.3 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 52 | 52 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 68.3333 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 318.4999 | 147 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.7 | 2.7 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.11 | 32.2 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1235 | 24.7 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3202.0833 | 145 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 282.3333 | 220 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.6 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.7499 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.45 | 87 | 1 | 2 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 405 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2010 | 150 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.85 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.3333 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.6666 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 177.6666 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191.6666 | 115 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 559.4167 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1564.3745 | 20.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1881.4998 | 318 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.75 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 367.5 | 175 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 760.25 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 850.6667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.05 | 73.5 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1275 | 150 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8550 | 150 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5473.1 | 458 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1331.6664 | 340 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1819 | 340 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 450.0833 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 580.1499 | 123 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 69.3 | 14 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1723.6667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2040.55 | 111 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 18.2 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1.2833 | 7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 40.25 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 651.9 | 159 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 32118.8 | 14 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 54.6833 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 0.26666 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 32.0667 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 38.2666 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 145 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 201.5833 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 0 | 0 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 18 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 73.7 | 33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 600 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 37.5 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 0.66666 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 16.4 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3034.205 | 12.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 28.29 | 20.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 17 | 60 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 50.05 | 14.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 85 | 60 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 0 | 0 | 1 | 2 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 10575.3333 | 58 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1212 | 72 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | RFC | Winter | 19.2 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 30.8333 | 74 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 462 | 210 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 4 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 8 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 29.1333 | 46 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 47.5333 | 23 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 5.9333 | 89 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Summer | 0 | 0 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Summer | 45.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 5.3666 | 46 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 41.3333 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 76.7 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 3410.55 | 53 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1800 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 0 | 0 | 1 | 2 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 9 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 44 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 199.4999 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 118.6666 | 89 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 21238.35 | 179 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 131 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 7194.6666 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 89910 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 461.8333 | 163 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1837.2 | 6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2259.8333 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 599.2667 | 35.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Summer | 56.7166 | 83 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Winter | 184 | 184 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Winter | 7375 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 6.6666 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 30.6666 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1071 | 210 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 645.8333 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Summer | 107.9667 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 0 | 0 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 22.7333 | 62 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 16.7833 | 53 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 10083.6667 | 13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 860 | Co-generator Block | RFC | Winter | 30 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 860 | Co-generator Block | RFC | Winter | 18 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 279 | 62 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1246 | 70 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 661.5 | 49 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 838.5 | 39 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2904.45 | 51 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 280.85 | 137 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 818.4 | 62 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3256.8 | 46 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 890 | 50 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1542.75 | 45 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 567.6 | 43 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2262.7 | 66 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2324.4 | 78 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3461.6666 | 62 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 4528.0966 | 139.9 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 850-Combined Cycle Block
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204 | 17 | 1 | 1 | 0362-Burner tilts | D1-Forced - Immediate | 100-Fossil-Steam
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.5833 | 49 | 1 | 1 | 0362-Burner tilts | D1-Forced - Immediate | 100-Fossil-Steam
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3788.9498 | 249 | 1 | 1 | 0362-Burner tilts | U1-Forced - Immediate | 100-Fossil-Steam
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21968 | 16 | 1 | 1 | 0362-Burner tilts | D1-Forced - Immediate | 100-Fossil-Steam
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 253.4 | 21 | 1 | 1 | 0362-Burner tilts | D1-Forced - Immediate | 100-Fossil-Steam
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 30117.6 | 41.83 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 27 | 60 | 1 | 1 | 0366-Duct burners (FBC only) | U1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 21 | 28 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 4337.52 | 5.83 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 227.2833 | 13 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 12363.12 | 46.83 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 34841.52 | 46.83 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 123.8 | 30.95 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 851-CC GT units
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2048.3333 | 100 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.75 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 109.182 | 105.66 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.3333 | 7.6 | 2 | 4 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20276 | 548 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3776.25 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1315.35 | 166.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 142.4 | 48 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.1407 | 43.46 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 275 | 150 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.675 | 39.21 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.8666 | 124 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.505 | 38.02 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.51 | 6.34 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 174.6633 | 85.9 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60.8 | 96 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1263.4664 | 412 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 157.6665 | 220 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.1 | 7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77.3333 | 116 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.8333 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 260 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2.6667 | 32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.6749 | 76.05 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31.698 | 105.66 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50.4 | 24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 553.5 | 246 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.8331 | 290 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2968.6663 | 610 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1827.8 | 703 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 235.6897 | 382.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.1683 | 19.01 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.9216 | 47.53 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132 | 66 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2569.7498 | 285 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 530.8329 | 650 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 160.55 | 57 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.8333 | 115 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170.5833 | 115 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 826.35 | 236.1 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 260.9332 | 412 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 197.6499 | 177 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 857 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.3367 | 19.01 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.9426 | 104.57 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.5 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 226.1666 | 115 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49689.4664 | 872 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 800.25 | 97 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 3967.9164 | 445 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.505 | 38.02 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.9167 | 1 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.9216 | 47.53 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.9217 | 6.79 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27.5 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.5665 | 178 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2741.0416 | 147.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 378 | 540 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 848 | 530 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 425.3333 | 232 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 914.55 | 469 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 329.6 | 412 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 111.55 | 97 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 499.1999 | 144 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.4333 | 7 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 270 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.3567 | 19.01 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 692.048 | 35.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126.4 | 48 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.5833 | 115 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.8675 | 44.55 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2659.9998 | 600 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41.2725 | 55.03 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5017.0667 | 32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 182.928 | 35.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 480 | 24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.5 | 62 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2420.25 | 63 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 384.5332 | 412 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 789.7 | 106 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5463.333 | 440 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 181.04 | 37.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 650-Fluidized Bed
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 186 | 37.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 650-Fluidized Bed
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 159.96 | 37.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 650-Fluidized Bed
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 32.24 | 37.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 650-Fluidized Bed
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 336 | 56 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 111.7667 | 7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 81.312 | 135.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 4.2 | 28 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 4.5 | 6 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Summer | 119.7875 | 64.75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1.1667 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 154.1666 | 62.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | RFC | Summer | 8.1667 | 2.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 333.4666 | 250.1 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 213.1333 | 139 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 60.8333 | 73 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 3.5 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 152.1 | 27 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 209.8333 | 10 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 346.3748 | 244.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 12.5 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Summer | 0 | 0 | 1 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Summer | 3.2375 | 64.75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 0 | 0 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 55.4999 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 88.75 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 261.3333 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 384.1333 | 86 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Summer | 1630.2 | 78 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 215 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 259 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 630 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 15.95 | 87 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 20.3 | 87 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 7.5833 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 108 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0375 | Burner instruments and controls (FBC light-off system) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 564.1667 | 50 | 1 | 1 | 0375-Burner instruments and controls (FBC light-off system) | SF-Startup Failure | 650-Fluidized Bed
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.7833 | 31 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.0333 | 22 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.3433 | 55.03 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29.9 | 23 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 225 | 108 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 472.5 | 63 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 603.25 | 95 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3130.9998 | 372 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 31620.6332 | 406 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1122.4 | 244 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122.4999 | 105 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 921.3333 | 40 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.6666 | 88 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252.0442 | 20.03 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 234.6 | 68 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 8.8 | 4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 375 | 150 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122.0333 | 2 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 322.4997 | 450 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.8333 | 19 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 316.25 | 115 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1000 | 120 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61.997 | 65.26 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 192.6666 | 170 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 388.6457 | 133.25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D3-Forced - Postponed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1483.4332 | 382 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 333.1999 | 147 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1775 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 271.9998 | 510 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15 | 20 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46.3833 | 23 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 738.66 | 284.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 370.5 | 19 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.6 | 34 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 384.75 | 171 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 68.25 | 63 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 523 | 523 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2312.5 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 725.8 | 382 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 129.6166 | 77 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.7512 | 31.37 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 16 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.3333 | 32 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44.5 | 178 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 184 | 230 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 163.8 | 63 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 321.75 | 45 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 64 | 4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 4299.505 | 788.9 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.0832 | 155 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 328.5332 | 352 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.75 | 45 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.6667 | 20 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 289.3332 | 280 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.3332 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.8 | 16 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 347.5833 | 97 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1020.8333 | 35 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.3999 | 372 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3669.1661 | 850 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 287.4666 | 112 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.95 | 77 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.6667 | 20 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 170 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 962.7999 | 199.2 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.1 | 34 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.6666 | 88 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 351 | 156 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.7667 | 14 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 300 | 150 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 655.0666 | 136 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.25 | 15 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4684.3331 | 299 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8188.3331 | 850 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 8 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.455 | 44.73 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96 | 48 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.2 | 84 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.3333 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 290.1333 | 136 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3879.9998 | 480 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 571.9999 | 312 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 6.6283 | 9.7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 9.1 | 26 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 29.5999 | 111 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 293.75 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 5.4166 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.3 | 33 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 99.3332 | 298 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290 | 100 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 102.6666 | 70 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195 | 39 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.95 | 9 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 420 | 140 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 227.3333 | 220 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 777.3333 | 220 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.2499 | 183 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 185.3999 | 108 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3021 | 318 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.6667 | 50 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122.4 | 54 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 274.4 | 196 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 928 | 120 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.9999 | 120 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 486 | 162 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22 | 440 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9239.25 | 635 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8001 | 635 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1197.8996 | 594 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1623.5998 | 594 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2595.1249 | 97.5 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1118.9499 | 417 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.3333 | 29 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 278.2833 | 59 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 435.4 | 84 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 446.25 | 85 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.6666 | 64 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.8333 | 34 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 215 | 86 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1831.3331 | 410 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 780 | 260 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1654.4 | 352 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 128.9166 | 65 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 202.1 | 141 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.8 | 68 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.4 | 96 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.0342 | 36.41 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 245 | 150 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 350 | 10 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 250.2 | 139 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 9720.7999 | 174 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 216.8 | 271 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78.3333 | 100 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 183.0026 | 343.13 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1243.3332 | 200 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.3333 | 100 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 71.5 | 130 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.6666 | 230 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.25 | 123 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 334 | 167 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 90.45 | 36.18 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 8 | 30 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 272.8 | 682 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.1666 | 130 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203.1666 | 115 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 248.3332 | 149 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2043.3 | 417 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2.9167 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.335 | 62.67 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 668.2666 | 112 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2793.7499 | 225 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.9333 | 104 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.1 | 21 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170.8333 | 82 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 815.8333 | 10 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 460 | 75 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 37.8667 | 32 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 549.3331 | 320 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.3998 | 264 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 227.3331 | 682 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7076.9998 | 630 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 653.6665 | 265 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 35.5333 | 26 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 806.1 | 268.7 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 38.5667 | 26 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2680.3333 | 17 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 16.6667 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.1666 | 70 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.6667 | 20 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1958.7998 | 249 | 1 | 1 | 0390-Burner wind boxes and dampers | SF-Startup Failure | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1615 | 34 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.2083 | 22.1 | 1 | 1 | 0390-Burner wind boxes and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 485.3333 | 80 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 124.5 | 30 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130.9 | 77 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248.9666 | 194 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 103.2 | 258 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 592 | 37 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 621.6 | 37 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1361.35 | 57 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3128 | 80 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.2533 | 23.2 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1396.5 | 98 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16205.2612 | 510.67 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 297 | 132 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7422.6665 | 380 | 1 | 1 | 0400-Burner wind box fires | U2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 497 | 70 | 1 | 1 | 0400-Burner wind box fires | D2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34163.823 | 510.67 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 262.2 | 57 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1410.2079 | 166.56 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 176519.1997 | 858 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1284.1666 | 46 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13892.6665 | 280 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 279.4867 | 45.2 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 616 | 70 | 1 | 1 | 0400-Burner wind box fires | D2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 729.1 | 27.6 | 1 | 1 | 0400-Burner wind box fires | D2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51328.3329 | 1300 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 258.07 | 59.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.2667 | 44 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.75 | 55 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 562.6247 | 136.67 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 119.5 | 10 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 26.22 | 11.4 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 460.5867 | 25.4 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 20.23 | 23.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 28.2217 | 28.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 143.1933 | 18.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 185.745 | 18.27 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 5.8333 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 142 | 21.3 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 193.9999 | 120 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.9999 | 90 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33.3333 | 80 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 353.3333 | 50 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1200 | 100 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 13.09 | 23.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 21.1467 | 12.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 179.275 | 21.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 36.9 | 24.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 77.5667 | 26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 75.02 | 34.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1140 | 60 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 17.9508 | 16.57 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 43.5435 | 18.27 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 110.0417 | 13.9 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 708.1666 | 70 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259.9 | 138 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.1667 | 35 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 770.8333 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.2 | 12 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1440 | 120 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 36.465 | 22.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 72.59 | 23.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 102.8417 | 28.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 21.541 | 16.57 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 164.7333 | 14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 139.5332 | 364 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1.1333 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 4.5 | 15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 245.05 | 13 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6118.5831 | 595 | 1 | 1 | 0410-Other burner problems | SF-Startup Failure | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17721.0165 | 313 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.0667 | 19 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.42 | 30.42 | 2 | 2 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.5 | 70 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 123.75 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 116.59 | 26.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 282 | 18.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 11.9 | 23.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 37.2292 | 17.87 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 180.6666 | 27.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 233.18 | 26.2 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 98.098 | 16.17 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1002.5 | 401 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7762.4 | 313 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 236.9 | 103 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 28.25 | 113 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2391.83 | 28.2 | 1 | 1 | 0410-Other burner problems | U2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2095.75 | 83 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27372.75 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 549.6666 | 85 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 380.3333 | 70 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21120 | 55 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 9.5583 | 15.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 72.075 | 15.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 36.8333 | 26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 57.6 | 48 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 382.9566 | 26.2 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3000 | 25 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1312.1333 | 104 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 251.3333 | 65 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5806.5 | 30 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 35.8875 | 13.05 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 21.9583 | 15.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 206.6633 | 23.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 64.554 | 18.27 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 57.4 | 287 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 71.2999 | 93 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110 | 44 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150.35 | 97 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.25 | 75 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 321.75 | 65 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 73.84 | 21.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 32.4133 | 22.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 43.665 | 21.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 14.5583 | 17.47 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 18.43 | 11.4 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 450 | 37.5 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 650-Fluidized Bed
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 189.6667 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 800-Miscellaneous
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 25.85 | 14.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1315.35 | 27 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 75 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 332.0833 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 39.15 | 26.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 5046.4 | 19 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 47.3167 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 24 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 36.1 | 19 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 11693.5666 | 53 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 41760 | 58 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 66.24 | 20.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 85 | 51 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 9290.5 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 114.5833 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 222.75 | 15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 58 | 116 | 2 | 2 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1579.725 | 107.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 224.2666 | 116 | 2 | 2 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 345.9499 | 111 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Summer | 64.75 | 64.75 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 90 | 180 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 162.7082 | 177.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 347.9999 | 180 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 9.9667 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80.5 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 89.1667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 98.7 | 94 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 385 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1140 | 120 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.7333 | 92 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.3333 | 16 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.3333 | 73 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99.1666 | 119 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 118.3333 | 71 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119.25 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 282.75 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 459.75 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.9 | 19 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 75.15 | 167 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.9999 | 105 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.9166 | 125 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 204.1667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 327.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 473.75 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 602.9167 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 696.6666 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 750.2 | 68.2 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2008.4999 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2083.9999 | 120 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 170.6666 | 64 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19.2666 | 34 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.6166 | 59 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 135.4375 | 49.25 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 301.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 293.3333 | 160 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72.7666 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 512.5 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 529.5333 | 94 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 15.2 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 278.4166 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 286.25 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 645.0333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1362.6667 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4.4333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12.65 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.3333 | 100 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54.1666 | 130 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 135 | 27 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201.0833 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 304 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 469.5833 | 115 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1571.6666 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1729 | 130 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 243 | 30 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1816 | 80 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11 | 44 | 1 | 2 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.72 | 40.24 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 140.9166 | 89 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 633 | 15 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 26.1 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51 | 51 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.2 | 48 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9696.6666 | 200 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.855 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.2666 | 104 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.25 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 465.35 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 524 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1882.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.9333 | 34 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.7667 | 22 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.1666 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 480 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 486.57 | 49.65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.5 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 3 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 16.5 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.0666 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.1667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 54.75 | 73 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.3333 | 100 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91.6666 | 110 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235.4999 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 452.6666 | 140 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 591.5 | 45.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 592.5 | 150 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 708.8666 | 62 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1507.9166 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2445.6666 | 110 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 119.4666 | 112 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 5.5 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 119.1666 | 130 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14.6667 | 44 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.5 | 130 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 64.1333 | 74 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 144 | 64 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1973 | 30 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2156 | 140 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 527.4 | 108 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9823.3332 | 200 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 14.4 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 25.3333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 26 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.5 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44 | 8.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.99 | 25.33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101.15 | 119 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 155.8333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 157.3333 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 720 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2.15 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.7273 | 25.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.6833 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.95 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 318 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 690.6666 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1527.6 | 67 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6998.25 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2.75 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.0833 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33 | 5.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36.4 | 52 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.6833 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.0833 | 85 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.9999 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 90 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 611.1666 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3723.75 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6143.9999 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 126 | 84 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 565.25 | 119 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 134.7166 | 59 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1196.6667 | 20 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.0295 | 2.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.8 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 42.3667 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168 | 42 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 178.7333 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 234.75 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 342.55 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 421.6666 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2322 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2421.3498 | 237 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 32.8666 | 68 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.1167 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180.5 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240.8333 | 85 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1882.1 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10523.5333 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3.7333 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5.1333 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.6666 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.3333 | 85 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 269.1666 | 170 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 653.3332 | 140 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 675 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 748 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1046.6666 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1250 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1743 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1827.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2039.5832 | 125 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 6 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 79.65 | 59 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 85.7999 | 99 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 138.4666 | 124 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1014.1667 | 50 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 8.1 | 27 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 12.9833 | 41 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 282.5999 | 108 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.3333 | 29 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 25 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.4 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 90.7499 | 99 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 793.75 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 935 | 66 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.591 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.413 | 54.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19 | 9.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.5 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.0833 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1013.15 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.75 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14.9333 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.8333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.8 | 162 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.75 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 121 | 22 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 155.8333 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170.5 | 110 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.1333 | 16 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 193.5833 | 115 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201.6667 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 301.5 | 135 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 483.98 | 69.14 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1164.5833 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1838.6666 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3067.1666 | 110 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2.8167 | 13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.0333 | 74 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200 | 100 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45 | 22.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 59.85 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88.9333 | 46 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103 | 51.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 139 | 34.75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 157.0666 | 124 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 786.75 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1025.0666 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2504 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5265 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 105 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3116.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.1667 | 13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 18.6666 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.5 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 25.6666 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34.2333 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.5833 | 85 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.25 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.75 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 214.6666 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 262.5833 | 115 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 272.3333 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 286.65 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 373.5 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 812.5 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1000 | 125 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1064.25 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2032.3333 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 59.1666 | 71 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.8333 | 25 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 232.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 111 | 74 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9.1 | 26 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 767.9167 | 25 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.113 | 1.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13 | 6.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 85 | 34 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93 | 124 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94 | 23.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 646.8 | 56 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.5 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 359.3333 | 154 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 561 | 56.1 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14.85 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15.2 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15.7666 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.75 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.25 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 84 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.5 | 110 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 239.0833 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 330.4166 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 341.55 | 99 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 538.75 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 639.6665 | 202 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2866.6667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.0667 | 44 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 45 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 75.3666 | 119 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 171.1666 | 79 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 35.7 | 42 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 112.25 | 449 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 52.8 | 99 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 12586 | 434 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 240.9166 | 59 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 224.25 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 20.4166 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 183.6667 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 228.85 | 69 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 6 | 9 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 74.75 | 69 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 88.45 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 190 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 682.6666 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3788.6667 | 20 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45 | 45 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1341.0833 | 55 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30 | 45 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 169.1666 | 58 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 245 | 60 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 100.4667 | 44 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 167.4166 | 49 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 203.4 | 54 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.9167 | 25 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 49637.4664 | 364 | 1 | 1 | 0420-Cyclone crusher | U1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 58.6667 | 44 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45 | 45 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 188.5833 | 73 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1595.8333 | 50 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 48.6666 | 73 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 441.6667 | 50 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 941 | 60 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 172.9167 | 25 | 1 | 1 | 0425-Cyclone dampers | D3-Forced - Postponed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1432.083 | 491 | 1 | 1 | 0425-Cyclone dampers | U1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.1666 | 55 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 187.9166 | 55 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1718.75 | 55 | 1 | 1 | 0425-Cyclone dampers | D3-Forced - Postponed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.75 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22 | 40 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.25 | 25 | 1 | 1 | 0425-Cyclone dampers | D3-Forced - Postponed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 599.8667 | 44 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.3 | 51 | 1 | 1 | 0425-Cyclone dampers | U1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 165 | 50 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224 | 32 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.25 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4614.7664 | 334 | 1 | 1 | 0425-Cyclone dampers | SF-Startup Failure | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2983.7332 | 334 | 1 | 1 | 0426-Cyclone air ducts | U3-Forced - Postponed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 788.6666 | 65 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 182.5833 | 35 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 146.6667 | 44 | 1 | 1 | 0426-Cyclone air ducts | D3-Forced - Postponed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78.75 | 45 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3242.25 | 99 | 1 | 1 | 0426-Cyclone air ducts | D3-Forced - Postponed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42 | 56 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44.9499 | 87 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 299.0833 | 97 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 375.8333 | 110 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14355 | 580 | 1 | 1 | 0430-Cyclone furnace | U2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137725.5 | 491 | 1 | 1 | 0430-Cyclone furnace | U3-Forced - Postponed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 989 | 43 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2476.5 | 195 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10950.3333 | 247 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21015.3331 | 580 | 1 | 1 | 0430-Cyclone furnace | U2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225.5 | 20.5 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.3333 | 70 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2184.1667 | 25 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73 | 18.25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 517.75 | 95 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.25 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 45 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.6666 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.5 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 148 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 246.6 | 54 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.1666 | 50 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.1667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.75 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 120.1666 | 70 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1329.1666 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 388.5 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 35.7 | 63 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 325.5 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 456.75 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 138.498 | 50.67 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 34.4167 | 35 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4512.1333 | 86 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.75 | 45 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.2666 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 45 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 50 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.75 | 45 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.6667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19.1667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.6666 | 100 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.99 | 6.11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8727.75 | 135 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.4 | 96 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.05 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.4167 | 41 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.1166 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.5 | 45 | 1 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.1333 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 45 | 2 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.1 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.1666 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6167 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27 | 45 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.75 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66.6667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 79.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6666 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240 | 9.6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 100 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.25 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.2667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.3333 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.0833 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 143.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 228.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 232.98 | 21.18 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 58.2 | 36 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.75 | 45 | 2 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.25 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.25 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.2166 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.6667 | 50 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17 | 17 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.0833 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.75 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21 | 70 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 100 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.9166 | 115 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.8333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 267.75 | 85 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 43.05 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 528 | 44 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.8505 | 40.27 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 320 | 40 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 203.5 | 37 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20600.5333 | 64 | 1 | 1 | 0435-Other cyclone problems | D3-Forced - Postponed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.6667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.91663 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.8333 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5833 | 55 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.25 | 45 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27 | 27 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.5 | 70 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61.25 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6667 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 19 | 38 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2924.25 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10044.4164 | 469 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.1695 | 1.13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.7333 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 7 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.6666 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.75 | 45 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.6666 | 100 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.9166 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.75 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 162.75 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 333.5 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8841.25 | 55 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 32.5 | 25 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6769.0664 | 334 | 1 | 1 | 0435-Other cyclone problems | SF-Startup Failure | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.05 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.0666 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.5 | 45 | 2 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.0833 | 61 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.4667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.75 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 384 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49.9999 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.5 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.5 | 50 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.4166 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.3333 | 55 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.0833 | 55 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12 | 12 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.75 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135.6666 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161.6667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1049.9999 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 60.8167 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 444 | 37 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1002.75 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7380.8333 | 85 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.25 | 45 | 2 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.7833 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.5 | 55 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.0666 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.8333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.3333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.8833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.25 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.9166 | 155 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.6666 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 124.4833 | 77 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1676.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.3333 | 40 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.6666 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.25 | 45 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.5 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.6666 | 100 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.3333 | 50 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.1666 | 55 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.5 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 855 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 31.45 | 37 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 36.75 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 42.6 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 334.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27 | 6 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 180.8 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 0.55 | 1 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 5064.3 | 153 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 55.2 | 69 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 69 | 69 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 84.5 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 97.9999 | 84 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 143 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 152.7333 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 189 | 84 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 452.4166 | 89 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 8154.8997 | 459 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 8.55 | 9 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 69.4166 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 264.3833 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 390 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 28.5 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 49.5833 | 119 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 77.3333 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 349.2666 | 169 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 813.9333 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 12.25 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 37.6 | 94 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 177.8667 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 427 | 244 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 722.8 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 149.6665 | 449 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 241.45 | 439 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 565.5 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1005.3333 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2659.8 | 429 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3848.5664 | 439 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 7.9167 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 11.6 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 45.5 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 20.7 | 69 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 57 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3679.6497 | 459 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 53.2 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 98 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 31.4666 | 59 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 39.1 | 69 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 45.75 | 9 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 39.5833 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 141.9 | 99 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 282.75 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 117.3 | 69 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1625.535 | 602.05 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2093.944 | 445.52 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.25 | 35 | 1 | 1 | 0440-Fuel oil pumps (general) | D2-Forced - Delayed | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114 | 45 | 1 | 1 | 0440-Fuel oil pumps (general) | D2-Forced - Delayed | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.4167 | 35 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 255 | 100 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1683.4997 | 390 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 262.56 | 87.52 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 794.75 | 85 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 74.95 | 149.9 | 1 | 1 | 0440-Fuel oil pumps (general) | SF-Startup Failure | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 933.5314 | 788.9 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 3970.9166 | 85 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 341.972 | 145.52 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 901.4999 | 90 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2376 | 240 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1650.432 | 110.52 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 37.6 | 48 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 82.3333 | 52 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 711.072 | 197.52 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 331.4999 | 153 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 1074.6 | 398 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 4140 | 240 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 3709.4399 | 217.35 | 1 | 1 | 0450-Fuel oil heaters | D1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Winter | 1554 | 126 | 1 | 1 | 0450-Fuel oil heaters | U1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7985.6 | 713 | 1 | 1 | 0450-Fuel oil heaters | U1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3969.0329 | 713 | 1 | 1 | 0450-Fuel oil heaters | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 476 | 70 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.5333 | 17 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 25.3333 | 38 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 112.5 | 30 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 495.8333 | 85 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 92.4 | 88 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 948 | 48 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.8333 | 85 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 207.4 | 61 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1206.3333 | 110 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 62.1833 | 41 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 560.7 | 89 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 61.6666 | 50 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2729.0541 | 270.65 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 102.7583 | 104.5 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290 | 20 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 555 | 185 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 245.5199 | 118.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 107.4732 | 131.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1816.3166 | 83 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1838.2 | 84 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D3-Forced - Postponed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 142.8732 | 147.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 6568.8 | 20.4 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.5 | 10 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.5 | 11 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.1666 | 350 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450.6666 | 130 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98.5 | 10 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79 | 158 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 425 | 150 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 760.5 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 20.2133 | 151.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Winter | 58.0166 | 59 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5403.973 | 547.7 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1928.5499 | 207 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.8333 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 695 | 139 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 105 | 15 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 144.8532 | 271.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 61.5 | 41 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1483.4999 | 207 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 106.25 | 25 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 333 | 111 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4690.3 | 93 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 116.0533 | 217.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 225.2133 | 101.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3083.2828 | 242.46 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4518.525 | 547.7 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5185.8333 | 175 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 806.4 | 64 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1294.1051 | 156.23 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3354.9998 | 330 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 123 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 17.71 | 96.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 457.0265 | 181.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Winter | 309.3332 | 128 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 1471.6333 | 98 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 29691.75 | 177 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D3-Forced - Postponed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 414.4 | 111 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 3404.4499 | 411 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 118.3666 | 106 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 547.9999 | 411 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 148.32 | 123.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.5 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 498 | 83 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17.1433 | 27.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 21.1865 | 181.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 40.8633 | 106.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1944 | 81 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 27.95 | 43 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3839.9161 | 781 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 36.3333 | 20 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 180.7666 | 58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 4057.083 | 455 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172 | 86 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.2 | 1 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 221.6666 | 100 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 63.7 | 26 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 5.0265 | 301.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 42.1599 | 81.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 110.16 | 81.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 27549.4999 | 165 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3726 | 207 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 61.8333 | 106 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 11610.9 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 101.5 | 15 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1103.7333 | 16 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 35.8132 | 268.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 59.9533 | 211.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 786.4999 | 171.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 113610.25 | 65 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Winter | 83.2 | 128 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 7612.3234 | 598.61 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3648 | 72 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 610.68 | 581.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 757.35 | 153 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1355.785 | 437.35 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 525.45 | 113 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 11754.6733 | 86.9 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 139.8 | 233 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 983.9633 | 139.9 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 1098.7665 | 238 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 495.9 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2.9757 | 1.13 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 260.3833 | 17 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 280.8 | 24 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 140.25 | 33 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 680.1666 | 154 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 97.75 | 23 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 486.3 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 353.3333 | 80 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 44.1873 | 16.78 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2014 | Gas | GG | 860 | Co-generator Block | NPCC | Off-Peak | 80.2316 | 52.9 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 860-Co-generator Block
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 113.6667 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 223.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.1667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.6667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.75 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177.9333 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192.5 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 364.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 330 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 345 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 494 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 510 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3064.8329 | 710 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 11199.75 | 411 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 595 | 850 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 195 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 237 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 291.5 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 352 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 552 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.75 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.2 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.3333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 267.1667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 280 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 318.2667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 175.5 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 675 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 756 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1087.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 297.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 133 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 165.9333 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 178.5 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 213.5 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228.6667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 326.6667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 463.8667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 602 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 900 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1026.6667 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1099.75 | 53 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175.1 | 103 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11083.9997 | 816 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.8333 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.6667 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 236 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 270 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 378.75 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 420 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.6666 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.2 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170.3333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.1667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 315 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 126.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 258.4 | 68 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2361.5664 | 406 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.5 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.5 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 12 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 96 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 156 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190.6667 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 213.75 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 406.25 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 415.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 743.75 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1161 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.3333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 268.8 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 291 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 346.5 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357.7 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 247.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 320 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30.0667 | 41 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8335.775 | 517.75 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34541.1 | 594 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5175.5999 | 171 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 3827.3667 | 47 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27 | 27 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.25 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.6667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 192 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 711 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1470 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.8 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.5 | 14 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.1333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.6667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 165.2 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240.6667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248.5 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 268.3333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 307.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 467.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.55 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 432 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2550 | 170 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43230 | 660 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.6667 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119.4 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 154 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 275 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 521.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91 | 14 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.4 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 152.5333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 448 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.5 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 342 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 887.25 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1597.5 | 54 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1374.1666 | 85 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 44772 | 390 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.5 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.25 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120.8333 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 207 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 243.75 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 326.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 374 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 510 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 544 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 665 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 892.85 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.75 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.5333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182.9333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240.3333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 294 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 306.5833 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 363.3667 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 487.6666 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 324 | 48 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 823.3333 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3968.25 | 195 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12359.1999 | 336 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5020 | 60 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 22570.15 | 769 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 804.3332 | 254 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 2362.95 | 267 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 524.6081 | 324.5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 5012.2666 | 254 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 223.5333 | 7 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1491.9566 | 60.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7078.5 | 45 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100 | 120 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 512 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1760 | 160 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3124 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2537.35 | 93 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12885.9163 | 505 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15942.5267 | 9.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 208 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 13146 | 120 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 214 | 107 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 613.2133 | 7.4 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 30.4 | 19 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 74657.9166 | 77 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 788.8 | 51 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | SF-Startup Failure | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.125 | 22.5 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2402.5 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17575.25 | 55 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 678.8832 | 161 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3631.4999 | 162 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7546.6667 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11304.6666 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 103.5 | 6 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 436 | 48 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3363.5 | 7 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35 | 5 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 133.2 | 12 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 162.75 | 31 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38714.8662 | 682 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 25031.4164 | 415 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65.1666 | 230 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69.6666 | 55 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 452.6665 | 280 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 979 | 11 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 189.8333 | 67 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1750.3333 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1755.0333 | 74 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 213 | 20 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240 | 80 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5070.6667 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.75 | 35 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 104 | 26 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 300 | 120 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2828 | 2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10966.6666 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1846.05 | 31 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 664.6666 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 16.3333 | 28 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 316 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 818 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1902.016 | 108.48 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 850-Combined Cycle Block
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1933.8665 | 392 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 850-Combined Cycle Block
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 766.5919 | 108.48 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 850-Combined Cycle Block
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 3541.6665 | 250 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1867.5665 | 626 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19099.0996 | 606 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U3-Forced - Postponed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 7266.1998 | 564 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1912.5 | 9 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10802.0831 | 625 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 310.25 | 73 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1354.1662 | 625 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18391.2 | 316 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5233.0667 | 22 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 27193.833 | 455 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2860.2664 | 346 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6528 | 510 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5298.1664 | 830 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3205.0166 | 103 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1605.6 | 223 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15383.3329 | 1300 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26490.8331 | 766 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38741.7332 | 364 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7410 | 325 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15210.6665 | 620 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16383 | 635 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 723.5323 | 571.21 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1449.25 | 85 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 580.8 | 44 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2973.9 | 138 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2837.25 | 195 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6614.85 | 627 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 937 | 20 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 800-Miscellaneous
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 164.406 | 24.91 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 45.09 | 1.67 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 119.25 | 4.77 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 213.75 | 2.85 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 85.96 | 3.07 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 44.35 | 8.87 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 495.6 | 4.13 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 4 | 4 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 41.36 | 1.88 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 339.84 | 4.72 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 14 | 2 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 146.81 | 2.77 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 258.1 | 2.9 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 128.26 | 2.42 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 979.7666 | 266 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 9398.6665 | 265 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 3522.6855 | 412.01 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 2505.8 | 268 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 726.6 | 484.4 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 775.2 | 114 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 969.22 | 168.56 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 139.1983 | 177.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 271.3498 | 243 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.45 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.7333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92.5167 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 264 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.11666 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.8 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.85 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.75 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.1 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.75 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.3 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.1333 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.1833 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.3333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.4 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.75 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.1167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.8667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.4 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 139.0667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232 | 29 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 368 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 455.6833 | 19 | 1 | 5 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 1 | 1 | 5 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 2 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.7333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.6 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.9167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.7 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.1333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.1 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.85 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32.4333 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 85.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 149.5 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 843.7332 | 448 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3957.5331 | 667 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.8 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 348.75 | 155 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.3667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.4667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.8333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.0833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.25 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.1833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.8 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.75 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.5 | 33 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1837.2667 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.2 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.33333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.43333 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 2 | 9 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.4 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 1.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44.95 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53.55 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 77.9 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 104.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 147.03 | 3.77 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 192 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 199.8 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 12322 | 61 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5650 | 250 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11 | 5.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.13333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 2 | 5 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.0333 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.6 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.65 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.2667 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.6 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.97 | 4.33 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.5833 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.1667 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.3333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.0667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.25 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.5 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 377.65 | 21 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.93333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.7 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.5333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.2667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.1 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40.04 | 3.08 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.75 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 120 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 176.9333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2202 | 10 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1007.9999 | 432 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.4667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.99 | 3.33 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.01 | 3.67 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.96 | 1.87 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.65 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.9167 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.98 | 9.14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.4 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 2.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.85 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.2667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.6667 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.6667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.9333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.0667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.4167 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108.4 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.45 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.25 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.5 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.35 | 3 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 1 | 2 | 19 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.75 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.2333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.85 | 3 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.1333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.5333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61.8 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67.5833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 82.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94.65 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 133812 | 81 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 654.1723 | 496.84 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.0333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.8 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.2 | 42 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.8333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.1 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.9 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.33333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.45 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.95 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.55 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.6 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.2333 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.5333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.1333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.6 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.8 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.35 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.1333 | 17 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.3 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.7 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103.7667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 193.5 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.15 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 355.25 | 21 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 585 | 39 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.6667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 1.5 | 1 | 5 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.5333 | 4 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22.7 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.05 | 2.55 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.0663 | 10.67 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.3833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96.1333 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15422.234 | 510.67 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 2 | 5 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.9333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.0167 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.8 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104.6 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.26667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.4 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.55 | 3 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.9667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 2 | 4 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.9667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 3.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.4667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.2667 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.6 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.4667 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.05 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.5 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.7 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.8 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.0333 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.5333 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.8 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.15 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 297.05 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.8 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.1 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.1 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 2.5 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.7333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.04 | 1.67 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.55 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89.9 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 98.1167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100.6667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 277.0133 | 59.36 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.8 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.1333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79.35 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.6 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.9167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.8667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.4 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.5333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.5 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.35 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.6 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.5 | 25 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.5833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.5 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77.7333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.7833 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228.6 | 18 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.05 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 3 | 2 | 5 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.55 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 1.25 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 2 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.75 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.6833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.7 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.6 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.8 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.0833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.4 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.05 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121.3333 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 140 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.9667 | 26 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.5833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124.2 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 135.96 | 11.33 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.76667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.1 | 3 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.45 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.45 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.6333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.7 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.4167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.7167 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.8 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.2 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.0025 | 90.67 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.5 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.6 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140.0667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 536.5 | 29 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3122 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.53333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.4167 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.01 | 1.67 | 1 | 3 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.7667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.4 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.05 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42.6833 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.98 | 8.14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 54570 | 51 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62.65 | 179 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 60.3493 | 59.36 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 3985 | 50 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3059.6665 | 268 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 112 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 133 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 682.4132 | 393.7 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 45494.3998 | 576 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 7410 | 260 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 541.45 | 154.7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3411.6664 | 460 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 766.9666 | 173 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8186.6665 | 307 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2240.3331 | 715 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42739.9998 | 600 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8341.6665 | 500 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 600 | 150 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.75 | 25 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1694.3333 | 65 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29569.583 | 515 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43492 | 524 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 91925.1662 | 715 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106288.6665 | 620 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191363.333 | 850 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 75.0666 | 225.2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 227191.2496 | 615 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 10741.3332 | 265 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 5 | 150 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | SF-Startup Failure | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3114.6666 | 146 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 90950 | 170 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 2476.4 | 164 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 99110 | 170 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 4674.4016 | 179.9 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 10285.95 | 141 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 2317.0999 | 174 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 1712.4999 | 150 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 76130 | 230 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1227.7749 | 109.95 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2457.75 | 113 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 46920 | 230 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1557.0166 | 103 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2401.6166 | 103 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1164.4999 | 102 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 158294.5 | 710 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 86052 | 404 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 11411.8331 | 598 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 22521.333 | 560 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2190.0666 | 266 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 416.8663 | 481 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 21841.9995 | 804 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 634.2331 | 359 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2079.9998 | 240 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1683.9998 | 240 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1702.5 | 227 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 500.5 | 143 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1350.9166 | 145 | 2 | 2 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 26.75 | 15 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 11337.3 | 171 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Summer | 11035.1666 | 146 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 5064.0833 | 67 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2701.8331 | 290 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | SF-Startup Failure | 852-CC steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 55.1 | 87 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 224.4 | 72 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.56 | 20.14 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 37.9833 | 53 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 650-Fluidized Bed
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 5076.8333 | 83 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 650-Fluidized Bed
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 163.3333 | 10 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 650-Fluidized Bed
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 30.0333 | 53 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 650-Fluidized Bed
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 31.7167 | 11 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1392 | 29 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 388.1665 | 274 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5884.1564 | 421.3 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 120009.9996 | 600 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 650-Fluidized Bed
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 39146.6666 | 160 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1752.9832 | 269 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2189.4163 | 559 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 380 | 380 | 2 | 2 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 75246.3331 | 380 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 16.07 | 160.7 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 2299.0332 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 42 | 168 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 2736.2906 | 168.56 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 7919.1666 | 170 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 162.8832 | 168.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Summer | 816 | 170 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Summer | 10443.7466 | 158.8 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 116.09 | 178.6 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Winter | 38659.2 | 192 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 1347.5 | 77 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 242.15 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Summer | 297.5 | 170 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 174.0916 | 160.7 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 346.6666 | 162.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 82.6666 | 155 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 1809.5 | 141 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 7101.465 | 59.22 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 232.2665 | 268 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 229.1 | 158 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2175.1332 | 158 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 39.5 | 158 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1400 | 80 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Gas | GG | 861 | CoG GT units | WECC | Summer | 8879.4624 | 222.45 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 861-CoG GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.5 | 30 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 458.8499 | 289.8 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2621.6662 | 715 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.6666 | 100 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 480.6665 | 280 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 23589.8 | 559 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 233.7499 | 165 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2006.3332 | 260 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 206.5 | 59 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 3615.6 | 184 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | RFC | Winter | 2193.75 | 195 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 855.2166 | 97 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2004.3 | 102 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 852-CC steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 2 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 6 | 2 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 2.4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 18 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.98 | 6.83 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 379.2 | 6.32 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.5 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.6 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.7 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101.5667 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 134.4 | 9 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.66666 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 2.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62.88 | 3.93 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102.0833 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 2 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 9 | 2 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21 | 4.2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35 | 35 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 390.04 | 13.93 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.9333 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65.5667 | 14 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.6664 | 400 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.75 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 2 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.6667 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.06 | 2.79 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89.9 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1833.7 | 66 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 1 | 4 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.0833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19 | 4.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.96 | 5.44 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.5 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.1333 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.1 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.8 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.33333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 1 | 2 | 4 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.5833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.8333 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.25 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.7 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.6 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.4667 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 7 | 2 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26 | 6.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.99 | 4.11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72 | 7.2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.1667 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.3333 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.05 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.9167 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.81666 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.99 | 1.33 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.01 | 1.67 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.9333 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 1.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.7 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75 | 15 | 1 | 1 | 0570-Other reheat steam problems | D3-Forced - Postponed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41 | 10.25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.3 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.65 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.9333 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215.1667 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2543.9166 | 89 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16 | 16 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.01 | 1.91 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.1 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94.6167 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 712.8 | 216 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 2.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 3.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.99 | 6.33 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.2333 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.99 | 1.11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.95 | 3.45 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2143.1667 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1321970 | 1300 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 2 | 2 | 5 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 4.5 | 2 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.9167 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.1667 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52 | 3.25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.2 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 1 | 2 | 14 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 3 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.4 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.5167 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19.02 | 3.17 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19.03 | 1.73 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52.1667 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.1667 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37 | 9.25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 8.8 | 16 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.4667 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.4 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.4 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.2 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.2 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.1333 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 551 | 30 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 1.5 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.5833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.2 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.98 | 1.33 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.9 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 82 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93.3333 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 515876.4 | 58.89 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 353.1999 | 264.9 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 29824.5 | 590 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Summer | 10713.3899 | 162.9 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Summer | 132.3333 | 158.8 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 63.75 | 75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | RFC | Summer | 70.3333 | 84.4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 46257.6 | 138 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | RFC | Summer | 15415.7065 | 234.4 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 72 | 160 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1524.9166 | 145 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 238.7667 | 38 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 413.3333 | 160 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1133.15 | 173 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 49.8666 | 136 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 113.5332 | 131 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 812.7166 | 121 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3202.7999 | 153 | 1 | 1 | 0580-Desuperheater/attemperator piping | U2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260 | 260 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 264 | 33 | 1 | 1 | 0580-Desuperheater/attemperator piping | D2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6387.2 | 96 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53 | 20 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 130.1332 | 128 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 199.7499 | 141 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.0666 | 71 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 842.1665 | 310 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1520.4164 | 445 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1919.8666 | 121 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 239.9333 | 244 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1187.0832 | 385 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.8 | 12 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72 | 144 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 99.75 | 133 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 136 | 80 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1155.7 | 82.55 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 262.4 | 82 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 441.8333 | 110 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 336.0832 | 185 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 510 | 120 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1410 | 300 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3614.2998 | 282 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 29606.85 | 13 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 410 | 164 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1024.0999 | 147 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12700.1664 | 842 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 2 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3112.6 | 394 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 91.1998 | 342 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 93.4999 | 330 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1532.6666 | 121 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 755.3 | 83 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 724.5 | 63 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11340 | 700 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33821.1996 | 564 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 109753.5 | 570 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 930 | 300 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 881.4 | 113 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.2737 | 43.67 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1207.4666 | 64 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 186 | 62 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4571.9996 | 540 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3382.4332 | 254 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 552.5 | 170 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73548 | 60 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1 | 1 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.6667 | 35 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 368 | 92 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 88.75 | 355 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 75.8333 | 5 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29330 | 700 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4002.0833 | 85 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2774 | 380 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 27.7333 | 52 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105.6 | 72 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 1 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 100.7997 | 378 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 105 | 105 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 21950.6665 | 404 | 1 | 1 | 0590-Desuperheater/attemperator valves | SF-Startup Failure | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95 | 30 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1461.333 | 548 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.6667 | 1 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3 | 1 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4 | 2 | 1 | 2 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20 | 4 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 53.3332 | 128 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 789.6666 | 46 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3251.5164 | 349 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 18.3333 | 55 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 196 | 98 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.25 | 65 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196.3333 | 62 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.7167 | 11 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 58.4 | 292 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 225.0831 | 365 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 8.3333 | 25 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1945.9533 | 126.91 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2628.3332 | 415 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13737.1665 | 635 | 1 | 1 | 0590-Desuperheater/attemperator valves | SF-Startup Failure | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11607.9998 | 240 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 0.8 | 0.64 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 62.5 | 50 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1.12 | 0.64 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 9395.85 | 9 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18726.1333 | 16 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5797.3333 | 80 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D2-Forced - Delayed | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123 | 10 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D2-Forced - Delayed | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 775 | 62 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 798.6666 | 80 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D2-Forced - Delayed | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126 | 60 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D2-Forced - Delayed | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2146.3583 | 45.25 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | U3-Forced - Postponed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 4.98 | 4.98 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1798.75 | 25 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 3139.05 | 9 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 288100 | 670 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11849.6 | 64 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323 | 57 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 12544 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1764 | 280 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2796.8499 | 183 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3624.8 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3036.75 | 45 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392.8666 | 83 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107.3333 | 92 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 872.0833 | 35 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8230.5 | 54 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5596 | 6 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5278.1333 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5414 | 40 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11916 | 54 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3968.7833 | 83 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2552.9999 | 90 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 69.8166 | 71 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 19.8 | 9 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 7857.0667 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D3-Forced - Postponed | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20081.9665 | 383 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 971.8666 | 296 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6840 | 90 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13003.2 | 541.8 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11015.6914 | 621.77 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1334.6665 | 440 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62322 | 312 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 43218 | 840 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 61.062 | 101.77 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26740 | 700 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 24.222 | 66.06 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 812.5 | 650 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39264.85 | 577 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37127.6665 | 620 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 123.4879 | 115.77 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2741.6662 | 700 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 5986.1 | 598.61 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1848 | 660 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4620 | 770 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29851.2497 | 825 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6520 | 815 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24763.7494 | 825 | 1 | 1 | 0640-Startup bypass system valves | U3-Forced - Postponed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1354.1664 | 650 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 229.3225 | 88.77 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6200.7998 | 552 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 22.3176 | 58.22 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 101.9333 | 22 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11678.3329 | 650 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2231.3 | 842 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 10128 | 240 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 7821.0666 | 278 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 59260.5665 | 419 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2615.9999 | 288 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29149.9996 | 1320 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | SF-Startup Failure | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3745 | 749 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | SF-Startup Failure | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 272.745 | 495.9 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | SF-Startup Failure | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 367716.7997 | 816 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19394.9991 | 1350 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | SF-Startup Failure | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 252 | 252 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | D1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2072.5665 | 621.77 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | SF-Startup Failure | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 456 | 228 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | D3-Forced - Postponed | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14409.9991 | 1320 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 361.2498 | 255 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | D1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7862.4997 | 750 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11406.8331 | 769 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129398.5 | 770 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 603.1999 | 156 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2425.5 | 770 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 379.3333 | 40 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1978.6666 | 106 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 646.8 | 66 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1287.8 | 141 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32599.4664 | 448 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U2-Forced - Delayed | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.0666 | 116 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 105.1667 | 2 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1235.1 | 46 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4085.2 | 84 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 5226.9 | 786 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 252.0061 | 24.91 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 237.79 | 25.8 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12197.0833 | 73 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19802.9999 | 252 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 61320 | 60 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1467.5833 | 55 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3122.25 | 69 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4118.1249 | 82.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 144 | 72 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 215.2499 | 315 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6318.7499 | 225 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 768 | 90 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 469.8 | 17.4 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210.7 | 7 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25456.1999 | 342 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13545.4166 | 95 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250.25 | 77 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 162122.1666 | 59 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 308.95 | 167 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4782.6666 | 85 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2893.3333 | 7 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1054.6666 | 140 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 572 | 260 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 36061 | 60 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15477 | 154 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5659.5 | 77 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67847.2666 | 77 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 298.9 | 98 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5787.8331 | 410 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 634.8 | 552 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4788.6666 | 55 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 129.2525 | 37.83 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D3-Forced - Postponed | 650-Fluidized Bed
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 27303.7598 | 340.8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 650-Fluidized Bed
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 211.6 | 184 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 113.85 | 99 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 125.35 | 109 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 41.6666 | 100 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 654.15 | 147 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 520.65 | 117 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1498.3331 | 290 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 832.0999 | 159 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 818.9333 | 166 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 246.25 | 197 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 141.1832 | 197 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 93.8832 | 131 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 163.75 | 131 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 22 | 10 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2343 | 44 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 877.7998 | 342 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49 | 49 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1274.1666 | 275 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1199.3332 | 257 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 28.0052 | 14.87 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2656.1998 | 342 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12144.1665 | 295 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.3333 | 100 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46134.1664 | 830 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3448.6 | 86 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 20570.333 | 470 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2769.8833 | 19 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2442.9166 | 275 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 843.5998 | 342 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2056.3329 | 620 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 850-Combined Cycle Block
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1687.6666 | 166 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 1087.5 | 290 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 508.9023 | 34.58 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 862-CoG steam units
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16241.6665 | 500 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18870 | 200 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 14496 | 453 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4742.5 | 175 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6953.9165 | 455 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 4202.8 | 15.8 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 650-Fluidized Bed
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 146.4 | 48 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2014 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 201.8333 | 35 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 852-CC steam units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 995.8666 | 308 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4662.5333 | 136 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 12293.6914 | 788.9 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1890.3333 | 106 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 480 | 120 | 1 | 1 | 0710-Blowdown system piping B | D2-Forced - Delayed | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 4351.3333 | 244 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 21300.6665 | 178 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3439 | 190 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1333.3332 | 250 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1032.4 | 232 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1908.1666 | 107 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 4092 | 620 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2640.1665 | 310 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1619.3332 | 140 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 851-CC GT units
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 13.9333 | 44 | 1 | 1 | 0720-Blowdown system controls / instrumentation | D1-Forced - Immediate | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 157.2 | 72 | 1 | 1 | 0720-Blowdown system controls / instrumentation | U1-Forced - Immediate | 851-CC GT units
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 447.6 | 72 | 2 | 2 | 0720-Blowdown system controls / instrumentation | U1-Forced - Immediate | 851-CC GT units
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9522.15 | 199 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5230.3833 | 199 | 1 | 1 | 0730-Other blowdown system problems | U2-Forced - Delayed | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3799.9999 | 240 | 1 | 1 | 0730-Other blowdown system problems | SF-Startup Failure | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 437.8332 | 185 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1895.25 | 63 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41059.0999 | 183 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.6333 | 50.75 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2105.9333 | 124 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3088 | 60 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2073.75 | 175 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 135.6664 | 370 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 16343.3333 | 50 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89424 | 69 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73729.6 | 812 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 514.9833 | 145.75 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 575.4333 | 122 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8650 | 60 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.2833 | 29 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296.2291 | 60.25 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 641.4997 | 384.9 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 875.5481 | 347.9 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 51285 | 65 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1096.6666 | 40 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5086.6666 | 140 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 43.9999 | 330 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.1665 | 407 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37870.2495 | 705 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 891.2581 | 562.9 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.0416 | 74.5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 234 | 24 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2582.3333 | 122 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9716.4166 | 65 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 5368.5333 | 112 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50362 | 298 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11156.25 | 525 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.95 | 27 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117.6833 | 23 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 226.6833 | 50.75 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6878 | 114 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.6 | 69 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8253.9333 | 46 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29876 | 60 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 601.5 | 90 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 80.5 | 230 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 81.4256 | 92.18 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 510.2167 | 23 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12058.134 | 332.18 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 114.6331 | 362 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1504.6666 | 122 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 179 | 60 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2846.6666 | 140 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 429.1667 | 50 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58916.3328 | 740 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4256 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1032 | 258 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4402 | 62 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 281.1666 | 60.25 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 526.9333 | 8 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41577.5316 | 61.1 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 74.9999 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1806.728 | 92.18 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4558.301 | 92.18 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 2083.6666 | 140 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 7379.1666 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 154.7331 | 422 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8528.189 | 510.67 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323.4 | 132 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 836.5 | 42 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7137.075 | 135.3 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 463.3332 | 200 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1096.942 | 92.18 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 32659.374 | 92.18 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 73752 | 84 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7833.6 | 816 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 352.6 | 164 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36937.5995 | 816 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3770.25 | 99 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5720 | 65 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 41.9999 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 135.3332 | 280 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 6141.5 | 142 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 807.3 | 414 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 1190 | 850 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11721.6 | 407 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 354.25 | 13 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 800-Miscellaneous
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 2022.2333 | 103 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 497.7999 | 114 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 999.9 | 66 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 851-CC GT units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 162.5 | 75 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 8048.63 | 63.4 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Summer | 750.75 | 49.5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23039.1 | 159 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2328.75 | 45 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12841.8 | 34 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 789.0666 | 88 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1372.75 | 57 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4412 | 80 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11903.65 | 69 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1678.1328 | 812 | 1 | 1 | 0741-Boiler recirculation pumps - motors | SF-Startup Failure | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8712 | 330 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 9917.6999 | 117 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21358.9999 | 159 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45627.9998 | 240 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7798.7666 | 86 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 88742.4998 | 330 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2835.5 | 530 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1434 | 90 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12970.25 | 87 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 41148.5665 | 298.9 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 303.75 | 135 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2181.25 | 75 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25268.2498 | 315 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2969.3329 | 680 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28867.333 | 530 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 308.5333 | 13 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 800-Miscellaneous
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1435.1666 | 218 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 477 | 318 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 1253.4525 | 172.89 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 850-Combined Cycle Block
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 5012.4 | 72 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 851-CC GT units
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Winter | 2269.5033 | 32.6 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 852-CC steam units
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 75565.12 | 55.2 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 4767.0833 | 85 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5042.9165 | 175 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12564.0663 | 532 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U3-Forced - Postponed | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 671 | 244 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144 | 90 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1837.5 | 750 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53014.1331 | 682 | 1 | 1 | 0760-Boiler recirculation valves | U3-Forced - Postponed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1190.1664 | 370 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 9820.4165 | 455 | 1 | 1 | 0760-Boiler recirculation valves | U2-Forced - Delayed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5680.2406 | 241.37 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 132.5 | 75 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 769.2333 | 94 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 892 | 60 | 1 | 1 | 0760-Boiler recirculation valves | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4461.6 | 858 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1904.4 | 552 | 1 | 1 | 0770-Other boiler recirculation problems | SF-Startup Failure | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 505.9996 | 552 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1412.9 | 142 | 1 | 1 | 0770-Other boiler recirculation problems | D3-Forced - Postponed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 975 | 750 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1467.6664 | 740 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2565.3328 | 740 | 1 | 1 | 0770-Other boiler recirculation problems | SF-Startup Failure | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 919.9996 | 552 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 258.4833 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 185.25 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 328.0333 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 194.1333 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 734.5 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 852 | CC steam units | TRE | Winter | 39.8666 | 104 | 1 | 1 | 0770-Other boiler recirculation problems | SF-Startup Failure | 852-CC steam units
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 595.8 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 131.4 | 292 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29400 | 245 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 328.5 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 130.6665 | 280 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2193.9666 | 79.3 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30372.5 | 150 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 191 | 191 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 853.0833 | 70.6 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 235.3333 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 631.6667 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 5344.5 | 105 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11281.5999 | 96 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48381.5998 | 342 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1787.5 | 143 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 516 | 258 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 863.9998 | 324 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 74.0998 | 342 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.4499 | 297 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9670 | 100 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 5598.6665 | 380 | 1 | 1 | 0775-Economizer piping | U3-Forced - Postponed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 10371.6 | 268 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 650-Fluidized Bed
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 364 | 13 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 712.8333 | 26 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 724.3333 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 563 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 430.6667 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 13223.1666 | 85 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 14031 | 90 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 11389.9995 | 804 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 2876.4999 | 165 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 2569.9666 | 163 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | TRE | Winter | 83963.6559 | 82.32 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 861-CoG GT units
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1361.25 | 55 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5569.6666 | 55 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8942.0833 | 55 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4811.5833 | 55 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 16110.9499 | 333.33 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2799.9999 | 150 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78227.4999 | 150 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1568 | 56 | 1 | 1 | 0782-Headers and caps | U3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 349.65 | 21 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68619.8328 | 770 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 1912 | 239 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U2-Forced - Delayed | 851-CC GT units
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 7.5 | 90 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21.2333 | 26 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 75.48 | 125.8 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7777.1 | 83 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2052.2666 | 148 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 104 | 96 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3858.75 | 175 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 2530.5666 | 44.5 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22472.3661 | 838 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6720.8 | 271 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3194.3997 | 396 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175 | 140 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 428.8332 | 310 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 520.8333 | 250 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8175.1998 | 528 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 134.7806 | 98.62 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16908.6663 | 520 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1859 | 132 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 88.6665 | 280 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17122.5 | 90 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1223.5996 | 552 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 9075.6665 | 380 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1938.1166 | 225.8 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 286.35 | 23 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 32.9667 | 23 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 8109.375 | 259.5 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2241.3485 | 186.52 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3326.2999 | 160.95 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 5315.2 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 481.0666 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 2726.4 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 151.7666 | 157 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 5574.4 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 575.3833 | 79 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 840 | 280 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1677.3332 | 340 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6068.9998 | 630 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 667.8 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1853.3498 | 303 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 132.5333 | 112 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1233.1 | 209 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 93.5333 | 46 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 12.75 | 45 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 276.18 | 276.18 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6286.5666 | 113 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.5666 | 46 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1923.75 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 631.2499 | 303 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1025.55 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1304.1665 | 626 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1311.75 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 303 | 303 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 317.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 344.25 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6113.3332 | 280 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10474.5666 | 154 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 299.6997 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 332.0998 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 715.5 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.7167 | 23 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.3333 | 25 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 794.9997 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 826.5 | 570 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1742 | 130 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 442.4998 | 225 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 206 | 103 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 44.1666 | 106 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 564.4498 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 612.1498 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2749.9998 | 600 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2327.7544 | 333.33 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1325.8332 | 215 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.8 | 83 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2900.976 | 139.47 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3496.0479 | 139.47 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62 | 248 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 300.3332 | 340 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1236.6665 | 280 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 972 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.6333 | 94 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108 | 48 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 567.1667 | 10 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2911.6666 | 100 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 848.4 | 303 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1794.3829 | 713 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 11.5 | 30 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1922.2028 | 333.33 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2.1333 | 2 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 11659 | 262 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 12.4345 | 186.52 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 2466.9332 | 176 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 137.1333 | 187 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 11696.4 | 152 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 15115.9333 | 172 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 8348.9166 | 95 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D3-Forced - Postponed | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 7430.5833 | 95 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | WECC | Summer | 1795.5666 | 166 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 861-CoG GT units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 1362.8999 | 126 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 862-CoG steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 1397.6666 | 28 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 187.4166 | 173 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 313.4998 | 495 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 876.7499 | 315 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 5044.85 | 619 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 104.4999 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1583.2958 | 274.56 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 225.4999 | 165 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1023.75 | 315 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 302.64 | 75.66 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2950.5 | 105 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 5095.7499 | 165 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 231 | 165 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 27.1333 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 29.3333 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 33 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 101.1333 | 148 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 387.5 | 155 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 13581.2999 | 153 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 301 | 140 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 853.9999 | 183 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1493.3333 | 175 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 39.25 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 204.82 | 37.24 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 1740.75 | 55 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 13.175 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Winter | 27.1333 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 70.525 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 26.4 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 31.775 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 167.1666 | 170 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 15.5 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Winter | 510.675 | 49.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 2087.4825 | 162.45 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 48.888 | 40.74 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 88.97 | 130.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 115.8099 | 187.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Winter | 27.8667 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 57.35 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 30.0667 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 819.2 | 96 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 15.5833 | 85 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 619.1166 | 121 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 769.8166 | 221 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 24.5 | 98 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 47.5 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 50.0733 | 81.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 38 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 2360.4 | 126 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 277.3332 | 128 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 699.9999 | 150 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 376.1666 | 61 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 46.4666 | 68 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1641.6666 | 100 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 7315 | 70 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 41.1665 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 252.0833 | 121 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 505.5999 | 96 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1244.25 | 105 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 9.9999 | 300 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 53.8333 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 2917.95 | 147 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2127.96 | 165.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 11.55 | 77 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 2758.9999 | 186 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 860 | Co-generator Block | SERC | Off-Peak | 44.1999 | 78 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | SERC | Winter | 7392.5332 | 167 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 136.3998 | 264 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | SERC | Winter | 2165.8 | 49 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 240.2666 | 272 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 25 | 60 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 271.9998 | 255 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 134.7499 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 580.6665 | 536 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 687.9998 | 240 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 489.4999 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 703.5 | 402 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 132.6 | 204 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 311.4999 | 105 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 192.8666 | 263 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 697.6664 | 364 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 274.05 | 261 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 393.2499 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Winter | 118.7516 | 165.7 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 61.75 | 142.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 367.7332 | 197 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 81.4416 | 168.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 168.5 | 168.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 94.6 | 172 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 28 | 70 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 69.9999 | 300 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Summer | 77.0665 | 289 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 384.9999 | 150 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 293.9999 | 180 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | SERC | Winter | 76 | 152 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 65.5 | 131 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 108.7666 | 251 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 281.7665 | 214 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Summer | 72.25 | 289 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 8.65 | 173 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 3323.1999 | 186 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 8.25 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 4447.0333 | 178 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 142.4 | 178 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 323.3665 | 178 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 133.5 | 178 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 46.5 | 62 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 229.1666 | 275 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 4.5 | 90 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | SERC | Winter | 3319.1037 | 34.58 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 1548.9666 | 62 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 49.6 | 62 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 315.9182 | 173.9 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1150.5 | 390 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 349.7115 | 395.9 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 6344.3999 | 306 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 123.2499 | 255 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1043.7 | 147 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 69 | 60 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 794.2998 | 282 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 16.6 | 166 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 225.428 | 40.74 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Winter | 109.2 | 168 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 160.875 | 58.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 191.3333 | 70 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Winter | 171.8166 | 169 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 80.826 | 134.71 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Summer | 88.6666 | 70 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2014 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 186.9 | 178 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 61.62 | 142.2 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 240.2166 | 203 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | WECC | Winter | 2056 | 160 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 114.4 | 143 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 102.7 | 158 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 852 | CC steam units | WECC | Winter | 1233.6 | 96 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 98.1083 | 96.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | SERC | Winter | 164.64 | 82.32 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25603.5 | 195 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U2-Forced - Delayed | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 131334 | 70 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 100-Fossil-Steam
0814 | In-bed bubble caps (FBC only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 3802.5 | 32.5 | 1 | 1 | 0814-In-bed bubble caps (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5 | 70 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 691.5 | 45 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 101.5 | 70 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.5 | 50 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1900 | 190 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2693.3666 | 98 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 29741.3 | 46 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 17565.6 | 312 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1659.2 | 51 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5126.3332 | 364 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26766.1332 | 364 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52365.15 | 491 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 540 | 90 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 5.1666 | 31 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1916.25 | 105 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2639 | 145 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16321.6666 | 100 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2748.3333 | 100 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15252.9999 | 210 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3390.9332 | 176 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4908.75 | 255 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8048.25 | 315 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 168441.1665 | 395 | 1 | 1 | 0820-Casing | D3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4581.6 | 265.6 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39087.5332 | 364 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7817.5999 | 168 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220 | 40 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 630.75 | 45 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 477.75 | 9 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3081 | 195 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1928.4 | 128.56 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1037.4 | 76 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2070 | 100 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46556.3333 | 190 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 89.5333 | 79 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 263.75 | 25 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14591.6666 | 100 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 25528.55 | 103 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.5586 | 128.56 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9120 | 240 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2740.1065 | 265.6 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1105.5 | 55 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 963.7499 | 225 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7037.9998 | 270 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8539.6664 | 340 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10760 | 200 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9775.5 | 147 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 14 | 21 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 800-Miscellaneous
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 71.05 | 21 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 800-Miscellaneous
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 1380 | 30 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 850-Combined Cycle Block
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 1980 | 30 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 850-Combined Cycle Block
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 3193.248 | 91.76 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 142 | 284 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 190.7666 | 194 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 80.1 | 267 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.579 | 17.97 | 1 | 1 | 0830-Doors | D2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2174.85 | 243 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1974.1665 | 515 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.1999 | 144 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 833.9664 | 394 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4730.3666 | 194 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 177.7331 | 344 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3822.6665 | 244 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.8833 | 119 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1328.6 | 364 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.1 | 374 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 2799.5 | 66 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 825.6333 | 94 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2890.9999 | 294 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.1083 | 97.9 | 1 | 1 | 0830-Doors | D2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1090.8333 | 85 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 146.9333 | 58 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 650-Fluidized Bed
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2070.9998 | 285 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 4935.6666 | 260 | 1 | 1 | 0830-Doors | D3-Forced - Postponed | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 455.5249 | 287.7 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 4.3332 | 260 | 1 | 1 | 0830-Doors | D3-Forced - Postponed | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | RFC | Summer | 7984.6 | 166 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | TRE | Summer | 5143.3499 | 153 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 1967.4999 | 150 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 4357.6666 | 170 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2014 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3059.7 | 141 | 1 | 1 | 0830-Doors | SF-Startup Failure | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 3281.0666 | 128 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 6185.4665 | 184 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.7 | 13.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.7733 | 155.2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 859.8333 | 70 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2178.75 | 415 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.3749 | 111.3 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.6933 | 90.4 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 44236.5166 | 131 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1064 | 14 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2051.28 | 14.8 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3980.5416 | 41.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75081 | 870 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1846.6666 | 200 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1078.8 | 93 | 1 | 1 | 0840-Refractory and insulation | U3-Forced - Postponed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 953.3333 | 57.2 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10300 | 20.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 513.975 | 8.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2084.98 | 36.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 278.4 | 9.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2805.5383 | 8.3 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 69488 | 404 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.6766 | 111.8 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 868.275 | 76.5 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.035 | 143.7 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520.8383 | 6.1 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6730.6683 | 52.7 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 946.6666 | 113.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 424.8 | 3.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8153.5999 | 192 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17647.8333 | 190 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.8 | 2.7 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.6 | 6.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4728 | 197 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8822.3166 | 197 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23720.8 | 199 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66.6499 | 129 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125.9299 | 154.2 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 598 | 26 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.6 | 77.8 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 732.5866 | 54.4 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 22262.5 | 325 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 3145.88 | 37.2 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | NPCC | Off-Peak | 1964.78 | 37.2 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 650-Fluidized Bed
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10887 | 191 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 53714.7333 | 31 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 194958.333 | 500 | 1 | 1 | 0845-Windbox expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 31050.9332 | 212 | 1 | 1 | 0845-Windbox expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 29291.8333 | 181 | 1 | 1 | 0845-Windbox expansion joints | U3-Forced - Postponed | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 21312 | 37 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 297 | 27 | 1 | 1 | 0847-Other expansion joints | D3-Forced - Postponed | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 465.3 | 47 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 36514.5 | 330 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2160 | 90 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | SERC | Winter | 437.5 | 50 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 861-CoG GT units
0848 | Inlet panel | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | NPCC | Off-Peak | 74.5833 | 5 | 1 | 1 | 0848-Inlet panel | D1-Forced - Immediate | 861-CoG GT units
0848 | Inlet panel | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 861 | CoG GT units | NPCC | Off-Peak | 73.8333 | 5 | 1 | 1 | 0848-Inlet panel | D1-Forced - Immediate | 861-CoG GT units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.3988 | 4.87 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 309.55 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1605.8333 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2227.6667 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 1130.4 | 36 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 627 | 19 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.6333 | 2 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 362.1667 | 2 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 2919.6833 | 31 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 135 | 27 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 324 | 18 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 475 | 19 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9317.9333 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.1233 | 4.6 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4526.4 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 1317.0833 | 29 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 4635 | 45 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1773.1 | 298 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.0317 | 4.1 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.4053 | 4.48 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.3352 | 4.49 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 522.5833 | 1 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 108.5 | 31 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 494 | 19 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 648 | 18 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 880389 | 243 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.7175 | 4.95 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.0942 | 6.35 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 929.3333 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 665.4 | 36 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 228 | 19 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 4 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3955.3332 | 340 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 746.8833 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2958.8333 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 3472.75 | 29 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 2490.5 | 17 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 598 | 23 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 945 | 45 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1902.8 | 268 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6377.55 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7568 | 88 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 123 | 3 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 261 | 18 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 343.9332 | 268 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.1497 | 4.22 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.1988 | 4.27 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.9663 | 4.42 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1763.6833 | 41 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 256 | 4 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1155 | 22 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 17362.1 | 238 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 800-Miscellaneous
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 13320.0665 | 238 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 800-Miscellaneous
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 4138.4 | 42 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Winter | 4857.3 | 42 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 1773 | 18 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.6666 | 40 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 29.4458 | 47.75 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.6 | 10.8 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 430.3833 | 119 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47228.9996 | 630 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 151.5 | 101 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.1667 | 5 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 159.4999 | 330 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24 | 6 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.8166 | 221 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97.3333 | 40 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.5 | 70 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 105.1458 | 25.75 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 757.2665 | 307 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1061.5 | 55 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.6 | 144 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 648 | 27 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 29.9 | 26 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27 | 6.75 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 91.6666 | 110 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.6197 | 1.13 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 220 | 220 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 82.8333 | 14 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 569.5 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1221 | 111 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5701.8499 | 231 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 408.3333 | 100 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 650-Fluidized Bed
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 172.5 | 45 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 52.5417 | 6.5 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 37.7916 | 90.7 | 1 | 1 | 0857-IP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 12105.3532 | 421.3 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 7868.25 | 117 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 850-Combined Cycle Block
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.4166 | 83 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 264 | 24 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 310.3333 | 20 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 708.5 | 130 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 273.96 | 15.22 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4460 | 80 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.1333 | 44 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 368.6666 | 70 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.2 | 57 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.6667 | 22 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255.0533 | 103.4 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 240.5 | 130 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.6 | 66 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5700 | 300 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1278.3333 | 130 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6348.3333 | 50 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5776 | 160 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4606.8331 | 422 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.16667 | 0.25 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1872 | 312 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 29.07 | 1.53 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3350 | 335 | 1 | 1 | 0870-Soot blowers - steam | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4100 | 40 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8.8667 | 38 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5820 | 194 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.6665 | 380 | 1 | 1 | 0870-Soot blowers - steam | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 615.3333 | 71 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4166.6664 | 400 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.8333 | 127 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340 | 400 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 383.3332 | 200 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5533.3328 | 800 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 146 | 73 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3724.5833 | 175 | 1 | 1 | 0870-Soot blowers - steam | U1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 315 | 36 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1477.6665 | 620 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 153.0667 | 7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 100 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 574.4166 | 61 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30 | 8 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 156 | 26 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 22.5 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 691.1666 | 290 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.5833 | 55 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 49.35 | 2.35 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3954.3666 | 194 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1420.3999 | 159 | 1 | 1 | 0870-Soot blowers - steam | U2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 333.3333 | 125 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1.3 | 1.3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 54.6 | 84 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 55.1565 | 17.51 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 437.1 | 145.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1309.9998 | 600 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10358.74 | 48.3 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1.8833 | 1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 793.3333 | 80 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 860 | Co-generator Block | RFC | Winter | 136.6833 | 139 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 860-Co-generator Block
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74 | 20 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 688.8 | 84 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 1 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 299.9166 | 59 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4.4 | 24 | 1 | 1 | 0872-Soot blowers - water | D2-Forced - Delayed | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1784 | 80 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64 | 40 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 244.6667 | 20 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 274.5333 | 142 | 1 | 1 | 0873-Soot blower drives | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 950.6665 | 184 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1691 | 190 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.25 | 3 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4402.08 | 183.42 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1367.8331 | 290 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 274.2 | 45.7 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.20833 | 0.25 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 384.1667 | 10 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 274.4 | 98 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 870.8333 | 190 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46.8166 | 53 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 20 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 399.4999 | 102 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.41665 | 25 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.6 | 8 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.6666 | 152 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1146.3333 | 190 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2702.6666 | 80 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2647.4 | 427 | 1 | 1 | 0876-Soot blower controls | U1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2150.9332 | 218 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1858.6666 | 82 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2175 | 181.25 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 185.5 | 35 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 636.7533 | 91.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1824.95 | 323 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2746.7074 | 137.91 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1282.5999 | 318 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.6 | 54 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 179.43 | 59.81 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 51 | 36 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 289.25 | 39 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1469.3333 | 38 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 182.5333 | 37 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 445.85 | 37 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.4166 | 53 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 189.8333 | 67 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 229.81 | 229.81 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 346.5 | 18 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2059.9998 | 600 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3996.96 | 249.81 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19820.8331 | 335 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 19.0667 | 13 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 25.8125 | 8.85 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 591 | 45 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 319.8333 | 95 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 738.4666 | 76 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1013.6499 | 145.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9569.1 | 334 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2237.34 | 159.81 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2250.0833 | 67 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 82.6667 | 32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 16.05 | 5.35 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 49.6598 | 10.31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1068.979 | 240.22 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | TRE | Summer | 9591.9167 | 47 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 4942.75 | 51 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1687.5 | 75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5140.5 | 298 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 816.6666 | 70 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.0667 | 8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 10 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169.2 | 72 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1133.3333 | 100 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4524.1666 | 305 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 122.6667 | 32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 7.4273 | 8.57 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 44.205 | 21.05 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.1666 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1129.9999 | 75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5179.2 | 312 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1875 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 543.9 | 37 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1794.4999 | 222 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6728.7998 | 312 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5241.6665 | 250 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19567.5 | 150 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 399.62 | 199.81 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 522 | 72 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 213.15 | 29 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 930 | 31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 73.3333 | 16 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 96.25 | 33 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120.75 | 105 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2968.3333 | 130 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.3 | 34 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210 | 40 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1371.25 | 75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 129.81 | 129.81 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3900 | 312 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 8 | 6 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2 | 8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | TRE | Off-Peak | 383.05 | 47 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 948.3333 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.1833 | 97 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7717.6968 | 167.11 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.7833 | 53 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 334.9333 | 8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 957 | 60 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2596 | 236 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Other | WD | 100 | Fossil-Steam | TRE | Summer | 8909.6333 | 47 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 10231.2 | 108 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 4201.3533 | 78.8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 38 | 38 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 792 | 88 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | SERC | Summer | 150 | 25 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 114.5083 | 9.1 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1120.5499 | 219 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 16836 | 368 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 561.5831 | 293 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 423.9999 | 318 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 654 | 218 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 5753.0665 | 368 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8974.9333 | 112 | 1 | 1 | 0885-Fly ash Removal System - wet transport | U1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.5 | 6 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1395.5332 | 242 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82.45 | 17 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2232 | 372 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D2-Forced - Delayed | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3296 | 412 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8129.1499 | 129 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3197.2665 | 199 | 1 | 1 | 0885-Fly ash Removal System - wet transport | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 633.3333 | 190 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 573.7832 | 173 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107 | 26.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 631 | 126.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 47.75 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 146.2166 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17756.6662 | 700 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | TRE | Off-Peak | 758.2667 | 47 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 899.5332 | 131 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 960.72 | 240.18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 642.4 | 160.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 807.88 | 21.26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 33.5833 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 189 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 146.4 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 11.3333 | 4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 84 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.6 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 693.55 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2599.25 | 281 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 793.98 | 132.33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22 | 5.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 311.0333 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 864.3833 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 435 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16026.0165 | 431 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 239.85 | 123 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 411.6666 | 100 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 290.95 | 1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1491 | 213 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 495 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1063.3 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.25 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400.15 | 151 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1489.2 | 146 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1600 | 320 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1 | 3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 167.9 | 69 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1314.1665 | 190 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11 | 2.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 667.02 | 111.17 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1382.95 | 81.35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1525.8832 | 319 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1680 | 210 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73440 | 816 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75163.9827 | 881 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 235 | 235 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 216.3333 | 110 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1691.9998 | 270 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2534.9332 | 224 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 561 | 187 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 54.12 | 27.06 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 458.58 | 76.43 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4747.5 | 225 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.3667 | 22 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.2 | 83 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3084.8 | 241 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5833.8331 | 290 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.8333 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 697.5 | 155 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1323 | 294 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1576.6664 | 430 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1674.1665 | 350 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6440.4998 | 330 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 202.54 | 101.27 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2043.68 | 255.46 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2738.97 | 210.69 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 317.7 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140.18 | 140.18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 460.5 | 307 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1287.5665 | 214 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24 | 8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 540 | 135 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 436 | 87.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 7107 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 106.5 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.9 | 6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65225.5997 | 816 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101053.4 | 812 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 30.3333 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 406 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 552.9333 | 88 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 3.3333 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 431.0666 | 53 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1174.8 | 88 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 28 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 76 | 38 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 91.8333 | 58 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 5078.6 | 268 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 14842.7332 | 268 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 24.1666 | 58 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 219.6999 | 78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 599.8666 | 88 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 196 | 98 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 378.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1356.7667 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1152.4 | 268 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 75 | 60 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 116.6666 | 40 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 180 | 48 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 458.2 | 158 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1211.5 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 352 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 6569.2 | 88 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 4.8 | 48 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 18.3333 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 48 | 48 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 206.5 | 118 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 940.5666 | 58 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 1260.75 | 123 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 138 | 138 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 167.7 | 78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 522.75 | 123 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 581.25 | 93 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 824.1666 | 115 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 2557.25 | 53 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 2695 | 98 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 189 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 190.6666 | 88 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 13784.1332 | 268 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 493.6333 | 118 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 1816 | 48 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 30 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 241.2 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 241.8 | 78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1216.55 | 87 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 39 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 40.8333 | 98 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 45.4667 | 8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 664.65 | 63 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1534 | 118 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 3024.2666 | 88 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | SERC | Off-Peak | 143 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 123.2 | 23.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 176.5833 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2434.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 358.8 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 139.5333 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 334.9667 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 30.5 | 6.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 65.12 | 11.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 96.0633 | 16.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | SERC | Summer | 48 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 93.6 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 531.05 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 133.705 | 12.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 139.5333 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 65 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 854.1 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 299 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | SERC | Off-Peak | 937.5 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 64.7833 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 268.83 | 26.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | SERC | Summer | 120 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 39 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 270.8333 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 120.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 4212 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 29.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 62.8333 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 68.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 279.0667 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 43.9833 | 9.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 293.3667 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 247 | 19 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 38.009 | 1.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 101.3333 | 12.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 174.5333 | 7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 433.0188 | 24.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 285.6602 | 10.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 314.42 | 15.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 874 | 19 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 931.2188 | 24.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 46.7875 | 5.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 125.68 | 4.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 147.356 | 5.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 545.0666 | 224 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3421.2332 | 197 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 530 | 265 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5323.1665 | 205 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1684.98 | 187.22 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365 | 150 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2160 | 240 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10070 | 530 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 468.75 | 125 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37247.85 | 459 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 61885.6664 | 815 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7565.4166 | 335 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 234 | 234 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2169.0666 | 224 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 500.1333 | 31 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177 | 177 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1812 | 151 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 158.3333 | 190 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5740.6832 | 271 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20153.3332 | 200 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 81.4667 | 47 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2685.3332 | 304 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7872.4999 | 201 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1265 | 230 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 322.9166 | 125 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1363.5 | 45 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 698.0999 | 234 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1802.6666 | 320 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8010.4332 | 334 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 381.3333 | 130 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 395.8333 | 125 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43037.4998 | 330 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 912.3333 | 119 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7374.9 | 117 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4700.2666 | 224 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 671.2499 | 225 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437.5 | 125 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 176.2367 | 9.1 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 90.6083 | 13.1 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 85.6917 | 9.1 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 199.8 | 11.1 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92.8 | 64 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4788.5 | 305 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 731.3999 | 207 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 996.4 | 94 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1566.6666 | 100 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2702.9332 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.6666 | 140 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.1666 | 107 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 154 | 154 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 756 | 252 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 970.3333 | 20 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43239 | 497 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54043.9166 | 145 | 1 | 1 | 0892-Bottom ash clinker grinders | U3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.1667 | 10 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 261.3333 | 112 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.3999 | 114 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4148 | 244 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1909.5 | 67 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1813.4998 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 845.8665 | 244 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2624.5332 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 319.5999 | 204 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3350.0998 | 234 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 715.7664 | 394 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7910.1665 | 310 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 959.9998 | 360 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 107.7666 | 106 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 540 | 135 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 757.8666 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3828.5 | 247 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3404.1665 | 190 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.3332 | 140 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 223.2 | 144 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 338.6666 | 127 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 431.25 | 125 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 440.5332 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 459 | 204 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 715.5 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2534 | 140 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2095.95 | 471 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2494.0999 | 294 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2965.9999 | 120 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1393.3332 | 152 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 62.7 | 38 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250.8332 | 215 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1836 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97 | 194 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1825.6 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3010 | 280 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.6666 | 37 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 209 | 209 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 385 | 100 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 470 | 12 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 102 | 12 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 487.7333 | 118 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5581.3332 | 460 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1338 | 223 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1525.4999 | 162 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3013.4666 | 194 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22741.4498 | 471 | 1 | 1 | 0892-Bottom ash clinker grinders | U3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 60.6667 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 377 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 110.5 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 93.1667 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 167.2667 | 26 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1586 | 26 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 39 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 370.5 | 39 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 52 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 223.1667 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 111.3667 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 3230.5 | 39 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 356.5 | 46 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4257.3332 | 155 | 1 | 1 | 0893-Bottom ash water pumps and motors | U1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 793.3332 | 280 | 2 | 2 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 422.9165 | 175 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2940.0683 | 103.1 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1315.9999 | 420 | 1 | 1 | 0893-Bottom ash water pumps and motors | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4316.8999 | 294 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.6 | 12 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5372.2666 | 224 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 746.6666 | 224 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210 | 28 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1146 | 120 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5372.2666 | 224 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1301.3331 | 320 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1200.4166 | 335 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3423.4666 | 224 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1462.6666 | 80 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4770 | 200 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 712.8333 | 91 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 451.25 | 36.1 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1568 | 224 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 696.6 | 38.7 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 575.3999 | 126 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 422.6333 | 62 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 543.75 | 75 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2186.6666 | 320 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5032.3329 | 620 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 520.1 | 74.3 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 361.3999 | 156 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.4 | 24 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2250 | 120 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 710.3665 | 422 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2720.6666 | 110 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2112.4999 | 75 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117.6 | 14 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 193.4293 | 90.67 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 476.7 | 9 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13496.3333 | 190 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 37.4 | 12 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10364.3332 | 340 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | D1-Forced - Immediate | 100-Fossil-Steam
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6950.1999 | 228 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 516.6165 | 223 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 432 | 24 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 392.4664 | 406 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 756.4999 | 267 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 334.3333 | 118 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1702.7832 | 271 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 288.0999 | 201 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 491.9999 | 144 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1380.3832 | 277 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43317.3 | 766 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6779.4999 | 105 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13729.8 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137.5 | 33 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 128 | 16 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 306 | 153 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 214.5 | 11 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 32.6333 | 17.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 158.8 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 198 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 255.2333 | 31 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 340.6666 | 70 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1028.2166 | 191 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 910.8 | 184 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 542.85 | 141 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5848.5 | 105 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1263.5 | 105 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3088.7499 | 105 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86.9167 | 35 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 154 | 110 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.6666 | 65 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 645.0666 | 118 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 736.6666 | 200 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1339.3332 | 245 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4779.1332 | 266 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3291.75 | 105 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11049.5 | 539 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40572 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 233.6 | 96 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 455.1 | 123 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 785.2831 | 371 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 830.1666 | 170 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1333.4 | 236 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 46712.4996 | 555 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14837.1998 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16562.9332 | 532 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.25 | 5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 829.4332 | 149 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 37 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2705.3666 | 293 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15038.1 | 539 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17257.8 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1134.7766 | 122.9 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 127.7833 | 41 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 56 | 16 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 799.2667 | 38 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2126.6666 | 200 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 184.3 | 194 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1562.6333 | 181 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3196.9998 | 345 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30144.7996 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1084.1333 | 94 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 81 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 297 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 638.6 | 31 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 677.6 | 308 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.5 | 21 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1257.8166 | 163 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1454.75 | 253 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 788.3666 | 134 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32591.3332 | 415 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 402 | 100.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174.5999 | 108 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 970.8333 | 250 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2713.2 | 408 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 456.8333 | 10 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 203.5666 | 31 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 123.5 | 30 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187.4667 | 38 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 363.05 | 53 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1426 | 184 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 111147.9996 | 555 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4312 | 539 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20212.5 | 539 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5895.75 | 105 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 650 | Fluidized Bed | RFC | Off-Peak | 240.75 | 45 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 418.1667 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 620.5333 | 13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 77.785 | 14.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Other | BM | 800 | Miscellaneous | SERC | Winter | 10947.2 | 66 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 477.75 | 13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 87.75 | 13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 483.1667 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 363.9735 | 8.91 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 2389.7067 | 14.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1826 | 30 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 577.8733 | 9.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 643.3263 | 10.91 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1115.7347 | 6.91 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 177.122 | 2.91 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 318.63 | 7.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.0833 | 65 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D2-Forced - Delayed | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 606.6665 | 208 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 229.3333 | 80 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 75 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27 | 36 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11521.2499 | 195 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276.5 | 79 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 869 | 66 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13613.5 | 190 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 531.5725 | 29.45 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10422.75 | 195 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3955.05 | 51 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36 | 18 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2967.2499 | 195 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | SF-Startup Failure | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7045.9999 | 195 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6435 | 195 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 337.7499 | 105 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1003.3333 | 175 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 713.7 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 418.1667 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1148.55 | 19 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 348.75 | 15 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1760 | 40 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1919.9999 | 180 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103.75 | 25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 188.75 | 75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 847.5165 | 241 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1040 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1722.5 | 265 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96 | 80 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 147.9166 | 71 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.25 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 920 | 40 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1213.3333 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4903.2499 | 165 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 93.15 | 23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.1666 | 70 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 417.5 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 732.5332 | 164 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56 | 28 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 195 | 32.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 216 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 784.08 | 32.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6129.2209 | 255.03 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24 | 6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.01 | 4.43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 175.6299 | 81.06 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 181 | 45.25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3127.66 | 183.98 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 42.1633 | 13.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 178.1033 | 23.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 56.338 | 16.57 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 370 | 37 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.6211 | 82.49 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.1248 | 76.81 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.6775 | 76.59 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21.5493 | 80.81 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.4775 | 113.91 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.681 | 68.74 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.2 | 77 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.4723 | 82.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.53 | 81.48 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 61.3609 | 85.62 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25.345 | 101.38 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26.4 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 29.0733 | 19.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 673.5666 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1500.75 | 261 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2467.7333 | 32 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.6283 | 5.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.75 | 75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109.9998 | 264 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 462.3333 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1057 | 70 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1320 | 165 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1680 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2489.1998 | 294 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4439.4 | 294 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52068.75 | 125 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 778.6666 | 320 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 931.2665 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 959.3333 | 40 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1215.9998 | 480 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3680 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.8 | 44 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.6666 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 186.4333 | 94 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 210.1666 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 280.8333 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 40 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 706.6665 | 265 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 749.7 | 119 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 852 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1209.7331 | 344 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1680 | 280 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7153.8833 | 119 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 273 | 54.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 362.88 | 15.12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 526.96 | 65.87 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 581.6666 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 601.0769 | 188.82 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36 | 6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 177.8533 | 133.39 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 292.98 | 48.83 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 310.96 | 38.87 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 440.04 | 36.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 14.3983 | 16.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 25.915 | 21.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 16.43 | 10.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 30.7545 | 18.27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.9167 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1880 | 235 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.778 | 99.26 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.9879 | 87.24 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.6213 | 81.79 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.05 | 77 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.2069 | 84.66 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 196.35 | 99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 974.2879 | 260.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42.6374 | 102.33 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 668 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | SF | Startup Failure | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 592.9 | 539 | 1 | 1 | 0920-Other slag and ash removal problems A | SF-Startup Failure | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1201.3332 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4735.5 | 770 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8846.5832 | 265 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96009.9996 | 600 | 1 | 1 | 0920-Other slag and ash removal problems A | U3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.8667 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98.2666 | 67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 162 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190.4 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 195 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 994 | 70 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1255.2167 | 7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1429.3332 | 268 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1925 | 275 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3126.6665 | 175 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3504.9999 | 150 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9176.05 | 743 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.5 | 30 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.5 | 75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 360 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 589 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 817.6 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 821.3332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2477.4999 | 150 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12.768 | 11.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.8917 | 16.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 124.2 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 529.9999 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 860 | 215 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1343.3332 | 200 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4290.8333 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.98 | 7.83 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 178.08 | 8.48 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 231.03 | 25.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 594.96 | 49.58 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 124.8683 | 68.11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 196 | 28 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1116 | 46.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 30.38 | 19.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2.1 | 2.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 345.1332 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.087 | 100.58 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.7525 | 123.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.315 | 72.63 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.315 | 82.63 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.4888 | 69.17 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.4004 | 161.19 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.7 | 82 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.2003 | 51.53 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39.3376 | 102.62 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78.2533 | 117.38 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5530 | 700 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16345 | 700 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85026.6662 | 700 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45425 | 500 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142373 | 770 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.4167 | 35 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 139.6333 | 71 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220.8332 | 125 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 856.4166 | 215 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1030.75 | 133 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1453.8333 | 61 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8250.2666 | 344 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.6 | 27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1939.8 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2077.6331 | 314 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10 | 8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21.2075 | 14.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68 | 34 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 164.2666 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 245.5666 | 53 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 240 | 40 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 450.1666 | 73 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 505.92 | 21.08 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 286.96 | 35.87 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 391.95 | 30.15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 33.8867 | 22.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.5316 | 121.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.15 | 77 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.5 | 77 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.6381 | 82.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.4373 | 83.32 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54.81 | 73.08 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1008 | 315 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 850 | 75 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1013.3333 | 40 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1443.75 | 105 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 676.35 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2263.3332 | 280 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5053 | 815 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.05 | 9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160.4166 | 55 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175 | 35 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 328.5 | 90 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.6 | 108 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450 | 225 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 530 | 265 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 709.3332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1154.8333 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2625 | 125 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17308.3332 | 250 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 578.6666 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 727.9333 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1809.4999 | 210 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.6 | 39 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.4999 | 90 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 166.7332 | 164 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 176.85 | 9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 271.6 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 578.6666 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 626.25 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1396.8 | 144 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1771.9999 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3599.1667 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39 | 39 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.97 | 6.33 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 313.98 | 52.33 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 447 | 44.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 654 | 27.25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1042.95 | 69.53 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10742.64 | 105.32 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.4583 | 87.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51.06 | 2.22 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 184 | 36.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 274 | 34.25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 993.06 | 55.17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 25.9467 | 13.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 82.44 | 22.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 29.0067 | 22.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 5214.2 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 668 | 167 | 2 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 660 | 330 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 668 | 167 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41 | 82 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.1025 | 73.47 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.7999 | 85.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3194.1 | 378 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.2872 | 134.42 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10638.8328 | 770 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2051.0828 | 815 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Other | WD | 100 | Fossil-Steam | TRE | Summer | 2962.5667 | 47 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.25 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.2 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 221.6666 | 70 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 383.1666 | 121 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 488.8333 | 35 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 655 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1290 | 215 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2789.5833 | 125 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 150 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 462.6666 | 40 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 882 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1190.9332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1219.9999 | 150 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5810.5663 | 598 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6196.2666 | 314 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7362.5832 | 265 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 414.5166 | 119 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 486.2 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1075 | 215 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.01 | 14.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 819 | 27.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1647.98 | 96.94 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2076.96 | 43.27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 225 | 37.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 367.7892 | 162.26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 418.04 | 29.86 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 643.02 | 91.86 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 991 | 99.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1341.99 | 103.23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8174.65 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.5374 | 142.89 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1264 | 316 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32.6775 | 130.71 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.0006 | 67.06 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51 | 51 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 114.0625 | 91.25 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 110.6691 | 120.73 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1430 | 260 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102039 | 602 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39571.5 | 555 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 244.1667 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 250.1666 | 95 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 420.3333 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1519.9998 | 300 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2106.9998 | 294 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.8 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.8333 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.8333 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 433.0666 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1060.6666 | 344 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1215.9333 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1849.9999 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.8 | 32 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 159.8 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 192.8499 | 87 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 280.9333 | 43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1209.6 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28 | 7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 256 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 104.01 | 34.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 142.02 | 23.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 143.12 | 71.56 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 455.5 | 227.75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 459.66 | 48.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 522.06 | 24.86 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 543 | 54.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2047.805 | 178.07 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 25.08 | 11.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 95.1933 | 26.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 1055.55 | 31 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4500 | 180 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.6 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.588 | 70.98 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.0703 | 62.47 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31 | 62 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.975 | 73.95 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37.4 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.8939 | 87.63 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 208 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 796.89 | 265.63 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 668 | 167 | 1 | 2 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20779.7331 | 736 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1976 | 57 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10301.45 | 179 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 562.5 | 225 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 732 | 61 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 984.1333 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1666.6666 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2693.75 | 125 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3694.6666 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85.2833 | 119 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.1 | 3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 539.4 | 124 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 673.1666 | 70 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 937.6666 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2098.1332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17625 | 235 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.5 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.75 | 75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 307.5 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 645 | 215 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 668 | 167 | 2 | 3 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 813.2667 | 44 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 183.99 | 61.33 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 696.96 | 38.72 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 463.97 | 35.69 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 583.02 | 32.39 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1460.72 | 76.88 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.4 | 68 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2762.5664 | 463 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.33 | 60.66 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.0583 | 84.14 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.7516 | 140.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 65.142 | 93.06 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.12 | 93.12 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.5019 | 80.46 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.7066 | 44.56 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2014 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.131 | 114.66 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 990 | 330 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1541.3332 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53033.3332 | 215 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80439.3328 | 770 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3247 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146466.8328 | 770 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 722.4 | 86 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2014 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 7638.6 | 58 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27056.9332 | 307 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 31.425 | 4.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 38 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 48.75 | 6.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 205.1 | 42 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 47.3667 | 14.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 135.0999 | 115.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 185.15 | 23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 24.5833 | 12.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 175 | 12.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 7.875 | 10.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 12.675 | 4.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 33.375 | 4.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 3150 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 77.0917 | 14.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 16.5 | 5.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 28.1417 | 5.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 210 | 35 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 1758.23 | 115.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 127.4 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 9844.4 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 376.3333 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 36553 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 112.6667 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 234 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Other | BM | 800 | Miscellaneous | SERC | Summer | 1785.3 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 20.5 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 29.45 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 5295.6 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2014 | Other | BM | 800 | Miscellaneous | SERC | Summer | 300247.2 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2014 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1697.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 48.79 | 6.97 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 238.65 | 6.45 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 805.35 | 12.39 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 2121.3733 | 152.8 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 908.01 | 47.79 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 42469.38 | 359.91 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2165.58 | 360.93 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 198 | 19.8 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2311.5 | 385.25 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 173.04 | 7.21 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6944.44 | 49.96 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 313.92 | 17.44 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 568.05 | 27.05 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3996.7 | 23.51 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1060 | 42.4 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1801.2 | 30.02 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0932 | Bed material transport tanks/hoppers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 27900 | 37.5 | 1 | 1 | 0932-Bed material transport tanks/hoppers | U1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 22318.2464 | 362.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 1136.5866 | 80.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 478.61 | 45.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 1267.7066 | 54.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 489.6266 | 48.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 1048.4133 | 65.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 155 | 30 | 1 | 1 | 0936-Bed material conveyors B | D1-Forced - Immediate | 650-Fluidized Bed
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 892.8 | 31 | 1 | 1 | 0936-Bed material conveyors B | D1-Forced - Immediate | 650-Fluidized Bed
0937 | Bed material mechanical separators and baghouse | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1613.3333 | 35.2 | 1 | 1 | 0937-Bed material mechanical separators and baghouse | U1-Forced - Immediate | 650-Fluidized Bed
0937 | Bed material mechanical separators and baghouse | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 260.8 | 26.08 | 1 | 1 | 0937-Bed material mechanical separators and baghouse | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | NULL | NULL | D1 | Forced - Immediate | 2014 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 48.6666 | 40 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 100-Fossil-Steam
0950 | Other bed material system problems | NULL | NULL | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 451.5 | 42 | 1 | 1 | 0950-Other bed material system problems | U1-Forced - Immediate | 100-Fossil-Steam
0950 | Other bed material system problems | NULL | NULL | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2001.49 | 42.6 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 100-Fossil-Steam
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 20.5 | 15 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 35.7666 | 37 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 5 | 50 | 1 | 1 | 0950-Other bed material system problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 21.75 | 15 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 415.4995 | 37.83 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 544 | 27.2 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 884.4 | 26.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 57.6 | 14.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 1547.34 | 125.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 136.3 | 13.63 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 7315.2331 | 293 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 23.4333 | 37 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 51.6666 | 25 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 57.9 | 19.3 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 5180.8566 | 35.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 148.05 | 27 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 157.7 | 38 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 367.2 | 21.6 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 285 | 19 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2014 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 3144.8666 | 293 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 18.9 | 27 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 28 | 14 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 200.2 | 14.3 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 42.3773 | 17.18 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 16.8 | 28 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 22.6167 | 23 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 140.4 | 23.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2014 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 36076.0399 | 349.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2014 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 210.625 | 37.5 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 12933 | 90 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 4186.4999 | 90 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2014 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 4527 | 90 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2014 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 987.9999 | 114 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Summer | 1246.2499 | 75 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 851-CC GT units
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2014 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1240 | 248 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 851-CC GT units
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 107716 | 28 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 852-CC steam units
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 60480 | 28 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 852-CC steam units
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 560 | 112 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 852-CC steam units
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2014 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1019.6667 | 38 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 852-CC steam units
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1018.1665 | 205 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1987.3 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4796.9998 | 351 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6166.0831 | 305 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 501.3833 | 67 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 628.05 | 159 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 631.25 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1374.3333 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4297.6 | 108.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 564 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 562.3333 | 14 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 129.1665 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 188.1 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 29792 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 183.75 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 4751.2666 | 124 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2014 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 7241.6666 | 275 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1897.6833 | 121 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4513.075 | 143.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 8040 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 13860 | 420 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1897.5666 | 58 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2652.0833 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4386.5332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5667.2 | 176 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6135.75 | 135 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11939.4 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13087.3331 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20226.6665 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29495.4666 | 248 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33579.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38376.083 | 515 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46311.6664 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47181.75 | 627 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51348 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66397.4995 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3881.9666 | 254 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4382.65 | 111 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5830 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6884.2666 | 112 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 8074.62 | 236.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9561.8665 | 184 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 9885.1646 | 238.58 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12627.9999 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13087.1666 | 155 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17688.2022 | 668.32 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20290.7833 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30639.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42675.7994 | 876 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83368.9997 | 780 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84669 | 780 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3692.5999 | 111 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4189.1 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4391.6666 | 155 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4461.264 | 242.46 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5379.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6556.3999 | 111 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7149.9998 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7641.3333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8026.6666 | 140 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8368.9333 | 92 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9432 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9441.605 | 132.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10766.1332 | 188 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10789.9999 | 249 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11778.856 | 241.37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17084.1 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 19447.355 | 144.59 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22284 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33706.6666 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41757.9165 | 515 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49753.5998 | 507 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78135.9998 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89678.3329 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113781 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2082.5 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7810 | 355 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 8086.8666 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 10528.4497 | 411 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 11539.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 18022.5 | 178 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 21706.6666 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 3652.4166 | 106.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2014 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 6571.9999 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11921.0664 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12415.2 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13224 | 551 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14180.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28961.3331 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141375 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5885.9832 | 191 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19476 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5231.2665 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2014 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 28856.5852 | 505.96 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7889.85 | 197 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15529.3704 | 264.63 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 59118.0442 | 466.66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81548 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19812 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20722.5 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2014 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23229.93 | 579.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam