## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Sum of EVENT_COUNT | Sum of DISTINCT_UNITS | Sum of MWLost | Sum of MWHrsLost
0020-Coal car dumpers; shakers; and unloaders | 11 | 11 | 1655 | 7388.2495
0022-Unloading/receiving hopper (train/truck) | 19 | 19 | 315 | 2308.75
0024-Rotary plow | 9 | 9 | 346 | 5970.6999
0028-Dust collection system | 10 | 10 | 1325.66 | 3998.5246
0030-Coal conveyors and feeders | 443 | 441 | 60769.51 | 575869.8897
0040-Coal elevators | 1 | 1 | 85 | 6240.4166
0050-Coal storage fires | 4 | 4 | 914 | 3588.2995
0060-Coal crushers including motors | 21 | 21 | 3940.75 | 28836.7684
0075-Storage silos/hoppers | 42 | 42 | 3806.5 | 56502.0603
0080-Stackers/reclaimers | 38 | 38 | 2676 | 41003.0495
0084-Coal conveyor scales-storage coal pile | 3 | 3 | 524 | 1900.9
0085-Bunker feeder coal scales | 5 | 5 | 532.77 | 1046.3231
0090-Bunker fires | 10 | 10 | 1021.82 | 18422.5932
0095-Bunker flow problems | 154 | 150 | 13210.76 | 153853.8052
0100-Bunker gates | 6 | 6 | 714 | 2936.8331
0105-Bunker structures | 7 | 7 | 323 | 9931.1499
0107-Screen (prior to bunkers) | 1 | 1 | 12 | 8
0110-Other coal fuel supply problems up through bunkers | 196 | 194 | 23303.52 | 311324.468
0111-Solid fuel feeder conveyors | 86 | 76 | 1953.63 | 15065.9706
0112-Solid fuel feed tanks/hoppers | 3 | 3 | 98.5 | 10634.4916
0113-Solid fuel tank/hopper fires | 3 | 3 | 29 | 247.4
0114-Solid fuel volumetric feeder | 86 | 80 | 477.04 | 3379.33
0115-Solid fuel gravimetric feeder | 10 | 10 | 194 | 1863.1166
0116-Solid fuel feeder motors | 1 | 1 | 67 | 3170.2166
0121-Other solid fuel feed problems | 89 | 82 | 1398.38 | 42396.6193
0125-Coal crusher dryer hammers | 3 | 3 | 475 | 6955.5832
0126-Coal crusher lube oil system | 1 | 1 | 125.66 | 379.0743
0127-Other coal crusher dryer problems (see code 0106) | 14 | 14 | 1773.98 | 26647.4561
0129-Other coal processing system problems | 46 | 46 | 3844.07 | 47651.6706
0132-Sorbent handling feeders | 3 | 3 | 84.15 | 1145.2533
0140-Sorbent handling screens | 1 | 1 | 33 | 97.35
0156-Other sorbent feed problems | 1 | 1 | 37 | 114.7
0163-Bed material feeders | 1 | 1 | 67 | 860.95
0200-Pulverizer exhauster fan (for indirect firing) | 32 | 32 | 2264 | 105815.6659
0205-Pulverizer exhauster fan drive | 14 | 14 | 850.7 | 20330.2164
0210-Pulverizer heater (for indirect firing) | 1 | 1 | 91 | 87.9666
0220-Pulverizer system cyclone separator | 1 | 1 | 150 | 572.4999
0230-Pulverizer bag filter | 1 | 1 | 140 | 340.6666
0240-Pulverized coal bin | 53 | 53 | 7913.85 | 48755.6681
0250-Pulverizer feeders | 1993 | 1985 | 188571.44 | 924580.1977
0253-Pulverizer feeder motor | 55 | 55 | 3847 | 16113.6304
0255-Pulverizer feeder coal scales | 27 | 27 | 3160.35 | 58161.2615
0256-Seal air system (air to pulverizers) | 35 | 35 | 6745.2 | 88912.5151
0257-Coal Crusher/dryer between feeder and pulverizer | 1 | 1 | 140 | 1617
0260-Primary air fan | 218 | 218 | 28772.19 | 534917.2434
0262-Primary air fan lube oil system | 18 | 18 | 4339 | 33005.8483
0263-Primary air fan drives | 49 | 49 | 4687.48 | 73650.6962
0264-Other primary air fan problems | 64 | 64 | 8938.94 | 83267.0067
0265-Primary air heater | 20 | 20 | 4295 | 178319.4416
0266-Primary air heater fouling | 16 | 11 | 308.53 | 14403.5599
0267-Primary air flow instrumentation | 58 | 58 | 9071.4 | 72026.2709
0270-Primary air duct and dampers | 185 | 185 | 18411.45 | 219249.4126
0280-Pulverizer fires | 104 | 104 | 10396.75 | 147693.7988
0290-Pulverizer reduced capacity due to wear | 178 | 178 | 10013 | 358022.197
0300-Pulverizer motors and drives | 159 | 159 | 14160.08 | 230768.9667
0310-Pulverizer mills | 1244 | 1238 | 112658.62 | 1452196.9141
0312-Pulverizer mill classifiers | 38 | 38 | 4544.5 | 83169.2917
0313-Pulverizer mill trunnion seals | 15 | 15 | 1049 | 11710.8331
0314-Pulverizer mill ball charger hopper (ball mills only) | 1 | 1 | 155 | 1219.3332
0315-Pulverizer mill coal level controls | 12 | 12 | 1029.31 | 4318.8041
0320-Foreign object in Pulverizers mill | 120 | 120 | 9711.57 | 71382.5243
0325-Pulverizer skidding | 16 | 16 | 996.1 | 14653.4263
0330-Pulverizer coal leak (pulverizers only) | 151 | 151 | 13348 | 134592.6044
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 140 | 140 | 12788.96 | 104730.4291
0335-Pulverizer lube oil system | 226 | 226 | 21969.11 | 134457.4882
0338-Pulverizer control systems (temperature and pressure) | 93 | 93 | 8851.15 | 46449.2508
0339-Pulverizer System Puff | 37 | 37 | 2838.99 | 69715.2138
0340-Other pulverizer problems | 751 | 748 | 69863.35 | 928944.724
0341-Pulverizer deluge system | 4 | 4 | 280 | 7905.1666
0342-Pulverizer inert system | 14 | 14 | 1528.72 | 6432.4647
0344-Pulverizer inspection | 131 | 131 | 9710.6 | 202683.7275
0345-Pulverizer overhaul | 61 | 61 | 3114.3 | 210672.6817
0346-Pulverizer pyrite removal system | 208 | 208 | 17165.48 | 76426.8262
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 166 | 166 | 16347.42 | 572235.2446
0358-Oil burner piping and valves | 11 | 11 | 1462 | 103844.6164
0359-Gas burner piping and valves | 112 | 112 | 18202.71 | 162473.903
0360-Burners | 226 | 226 | 16401.86 | 394623.1902
0362-Burner tilts | 3 | 3 | 623 | 18079.8329
0365-Bed warmup burners (FBC only) | 1 | 1 | 136 | 38553.7333
0366-Duct burners (FBC only) | 16 | 16 | 709.9 | 3077.9448
0370-Burner instruments and controls (except light-off) | 161 | 158 | 20371.19 | 256616.4165
0380-Light-off (igniter) systems (including fuel supply) | 90 | 89 | 20138.21 | 246190.4073
0385-Igniters | 82 | 82 | 14430.27 | 139880.0622
0390-Burner wind boxes and dampers | 25 | 25 | 3619.4 | 33415.3909
0400-Burner wind box fires | 10 | 10 | 1985.9 | 211564.8831
0410-Other burner problems | 108 | 93 | 6678.1 | 65612.6611
0415-Cyclone feeders | 205 | 203 | 14190.13 | 165046.9595
0420-Cyclone crusher | 11 | 11 | 422 | 2735.4165
0425-Cyclone dampers | 82 | 81 | 3496.93 | 49547.1495
0426-Cyclone air ducts | 4 | 4 | 405 | 16688.4165
0430-Cyclone furnace | 10 | 10 | 1892.2 | 34298.116
0435-Other cyclone problems | 299 | 196 | 13797.56 | 63471.9003
0440-Fuel oil pumps (general) | 10 | 10 | 2068.75 | 8755.3411
0441-Fuel oil pumps (burner supply) | 11 | 11 | 1969.48 | 55557.1247
0442-Fuel oil pumps (forwarding/transfer) | 1 | 1 | 202 | 898.9
0450-Fuel oil heaters | 2 | 2 | 331 | 2147.5833
0460-Fuel oil atomizers | 24 | 24 | 2255.58 | 29398.2691
0470-Oil and gas fires | 12 | 12 | 1326.4 | 16681.1161
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 69 | 67 | 10580.04 | 250295.1381
0500-Main steam piping up to turbine stop valves | 119 | 119 | 12452.91 | 678335.7747
0510-Main steam relief/safety valves off superheater | 61 | 57 | 7317.78 | 217046.4926
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 44 | 44 | 14247.01 | 501210.9832
0530-Other main steam system problems | 167 | 166 | 5856.9 | 122591.393
0540-Hot reheat steam piping up to turbine stop valves | 81 | 78 | 4929.74 | 448368.5502
0541-Cold reheat steam piping up to boiler | 18 | 18 | 4336.6 | 575151.1851
0550-Reheat steam relief/safety valves | 22 | 22 | 2491.96 | 96804.7388
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 33 | 33 | 6092.83 | 71246.8988
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 13 | 13 | 3032.8 | 78076.6754
0570-Other reheat steam problems | 108 | 107 | 7335.34 | 630970.4702
0580-Desuperheater/attemperator piping | 8 | 8 | 1223 | 27473.8666
0590-Desuperheater/attemperator valves | 44 | 44 | 9139.94 | 173090.9751
0600-Desuperheater/attemperator spray nozzles | 1 | 1 | 352 | 3825.0664
0620-Other desuperheater/attemperator problems | 28 | 28 | 2309.7 | 474162.3312
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 3 | 3 | 1500 | 55969.3329
0640-Startup bypass system valves | 40 | 40 | 22367.4 | 727918.9925
0650-Startup bypass tanks or flash tanks | 3 | 3 | 1410 | 40642.9161
0655-Steam by-pass system instrumentation and controls | 3 | 3 | 1427.9 | 11555.4666
0660-Other startup bypass system problems | 8 | 8 | 4048.8 | 71883.692
0670-Feedwater piping downstream of feedwater regulating valve | 15 | 15 | 1829.32 | 48555.193
0680-Feedwater valves (not feedwater regulating valve) | 37 | 37 | 7012.3 | 253126.9972
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 12 | 12 | 3908 | 28212.8156
0700-Blowdown system valves A | 17 | 17 | 4385.61 | 127301.1564
0710-Blowdown system piping B | 16 | 16 | 3233.15 | 87187.5938
0720-Blowdown system controls / instrumentation | 8 | 8 | 1797 | 1710.1161
0730-Other blowdown system problems | 7 | 7 | 2050 | 63474.3662
0740-Boiler recirculation pumps | 69 | 69 | 12404.9 | 593417.6904
0741-Boiler recirculation pumps - motors | 130 | 123 | 13921.05 | 1690664.5128
0742-Boiler recirculation pumps - motors - cooling system | 10 | 10 | 1838 | 95620.7827
0750-Boiler recirculation piping including downcomers | 6 | 6 | 698.9 | 20540.4531
0760-Boiler recirculation valves | 12 | 12 | 4227.37 | 97637.1401
0770-Other boiler recirculation problems | 59 | 59 | 8768.4 | 61370.5611
0775-Economizer piping | 32 | 32 | 4601.56 | 254403.4104
0780-Headers between tube bundles | 1 | 1 | 55 | 6424
0782-Headers and caps | 5 | 5 | 976.97 | 37757.4266
0790-Pipe hangers; brackets; supports (general) | 2 | 2 | 547 | 43042.1667
0799-Other miscellaneous piping system problems | 22 | 22 | 5202.6 | 134806.4879
0800-Drums and drum internals (single drum only) | 94 | 94 | 21104.44 | 288451.5905
0801-HP Drum (including drum level trips not attributable to other causes) | 72 | 72 | 11102.65 | 81412.8194
0802-IP Drum (including drum level trips not attributable to other causes) | 36 | 36 | 5935.43 | 27052.9369
0803-LP Drum (including drum level trips not attributable to other causes) | 22 | 22 | 3120.16 | 6450.3062
0810-Boiler supports and structures (use code 1320 for tube supports) | 2 | 2 | 599.1 | 91621.2998
0814-In-bed bubble caps (FBC only) | 1 | 1 | 32.5 | 538.9583
0820-Casing | 48 | 48 | 8440.01 | 1448028.4762
0830-Doors | 23 | 23 | 3776.51 | 96132.386
0840-Refractory and insulation | 50 | 50 | 5443.5 | 889688.8334
0845-Windbox expansion joints | 1 | 1 | 63 | 822.15
0847-Other expansion joints | 16 | 16 | 2648.22 | 182359.3135
0848-Inlet panel | 1 | 1 | 137 | 6612.5332
0850-Other internal or structural problems | 23 | 23 | 1720.71 | 289982.9816
0855-Drum relief/safety valves (Single drum only) | 24 | 24 | 2773.08 | 107373.0006
0856-HP Drum relief/safety valves | 1 | 1 | 78 | 2137.2
0857-IP Drum relief/safety valves | 2 | 2 | 390.6 | 252.9731
0859-Tube external fins/membranes A | 7 | 7 | 1151.39 | 98322.8682
0860-Soot blowers - air (see code 3844 for air delivery system) | 19 | 19 | 660.95 | 8616.3345
0870-Soot blowers - steam | 38 | 38 | 4826.43 | 142850.2382
0871-Soot blowers - sonic | 1 | 1 | 32 | 344
0872-Soot blowers - water | 3 | 3 | 339.8 | 2799.4849
0873-Soot blower drives | 2 | 2 | 99 | 195.6833
0876-Soot blower controls | 15 | 15 | 1630.8 | 25064.9828
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 97 | 97 | 9775.83 | 296820.6053
0885-Fly ash Removal System - wet transport | 13 | 13 | 2111.81 | 232985.6727
0890-Bottom ash systems (wet or dry) | 126 | 126 | 10558.22 | 227750.97
0891-Bottom ash hoppers (including gates) | 25 | 25 | 6218.15 | 325119.8431
0892-Bottom ash clinker grinders | 63 | 59 | 10430.91 | 160759.0927
0893-Bottom ash water pumps and motors | 9 | 9 | 3005.1 | 105618.606
0894-Bottom ash piping and valves | 26 | 26 | 5230.89 | 210132.3945
0896-Bottom ash dewatering bin system; instruments and controls | 1 | 1 | 180 | 734.9999
0897-Bottom ash rotary (drag chain type) conveyor and motor | 89 | 89 | 13915.21 | 343823.5702
0898-Bottom ash pyrite hopper (pulverizer reject) system | 6 | 6 | 1579.2 | 23114.0559
0899-Bottom ash controls and instrumentation | 4 | 4 | 93 | 990.25
0900-Slag-tap (cyclone furnace) | 21 | 21 | 3161 | 190420.6156
0910-Slag-tap (other than cyclone furnace) | 2 | 2 | 160 | 576
0920-Other slag and ash removal problems A | 241 | 228 | 23824.97 | 467915.0433
0930-Bed material coolers | 17 | 17 | 1453.65 | 23921.3231
0931-Bed material transport piping/valves | 6 | 6 | 2013.04 | 52805.9466
0932-Bed material transport tanks/hoppers | 1 | 1 | 129.8 | 3084.9132
0933-Bed material fans/blowers | 6 | 6 | 624.4 | 12701.2765
0936-Bed material conveyors B | 1 | 1 | 293 | 7129.6666
0950-Other bed material system problems | 24 | 24 | 3181.4 | 26523.3492
0989-Other bed solids recirculation problems | 15 | 15 | 1503.25 | 129757.7736
0991-Tube leaks | 4 | 4 | 442 | 27603.2833
0999-Other heat exchanger problems | 2 | 2 | 161 | 730.8
1000-Waterwall (Furnace wall) | 834 | 834 | 258588.21 | 19095470.3943
1003-Steam generating tubes between steam drum and mud drum | 25 | 25 | 6779.67 | 481039.348
1005-Generating tubes | 32 | 32 | 3422.1 | 293349.5725
1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | 1 | 1 | 155 | 21888.5832
1010-Cyclone furnace (in cyclone area only) | 28 | 28 | 5174.45 | 340253.5498
1020-Convection pass wall (water tubes only) | 38 | 38 | 13957.7 | 879847.2963
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 22 | 22 | 4473.93 | 463118.8347
1035-Platen superheater | 38 | 38 | 18268.2 | 2583778.2704
1040-First superheater | 216 | 216 | 51159.86 | 4105630.8136
1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | 1 | 1 | 268 | 27001
1050-Second superheater | 214 | 214 | 59746.28 | 4442319.0177
1055-External superheater link tubing | 6 | 6 | 2630.86 | 148028.7031
1060-First reheater | 202 | 202 | 76578.05 | 6935070.4972
1070-Second reheater | 60 | 60 | 23097.81 | 2385234.6432
1075-External reheater link tubing | 2 | 2 | 356 | 17201.9999
1080-Economizer | 235 | 235 | 49785.67 | 3619572.8128
1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | 2 | 2 | 680 | 28196.7498
1090-Other boiler tube leaks | 179 | 178 | 44644.26 | 3961539.3974
1100-Waterwall (Furnace wall) | 83 | 82 | 8154.55 | 424949.2529
1103-Steam generating tubes between steam drum and mud drum | 2 | 2 | 1193 | 73009.75
1105-Generating tubes | 22 | 22 | 373.8 | 38216.005
1110-Cyclone furnace (in cyclone area only) | 2 | 2 | 674.8 | 32390.3997
1130-Boiler screen; wing wall; or slag screen (water tubes only) | 10 | 10 | 989.92 | 192265.1387
1140-First superheater | 95 | 95 | 6811.6 | 283325.1183
1150-Second superheater | 116 | 115 | 12996.53 | 320157.5772
1160-First reheater | 67 | 67 | 6410 | 295697.4479
1170-Second reheater | 3 | 3 | 154 | 6530.8833
1180-Economizer | 45 | 45 | 4226.5 | 261400.957
1190-Other tube slagging or fouling | 179 | 179 | 11190.43 | 295119.0378
1191-Bed agglomeration (FBC only) | 2 | 2 | 149.2 | 10463.8933
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 31 | 31 | 2328 | 137765.9992
1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | 3 | 3 | 554.75 | 9363.6791
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 3 | 3 | 85 | 1927.9166
1310-Water side cleaning (acid cleaning) | 1 | 1 | 491 | 14910.033
1320-Tube supports/attachments | 1 | 1 | 542 | 131191.1
1330-Slag fall damage | 2 | 2 | 1276 | 72245.5496
1340-Tube modifications (including addition and removal of tubes) | 4 | 2 | 364 | 23855.9332
1350-Other miscellaneous boiler tube problems | 297 | 200 | 10951.2 | 451221.9236
1360-Boiler drains system | 13 | 13 | 3179.7 | 154478.1806
1400-Forced draft fans | 316 | 314 | 40205.47 | 1531477.6997
1401-Forced draft fan dampers | 32 | 32 | 5884.7 | 48574.1688
1407-Forced draft fan lubrication system | 13 | 13 | 2964.37 | 65944.7868
1410-Forced draft fan motors | 135 | 134 | 18246.29 | 1610828.4124
1411-Forced draft fan motors - variable speed | 17 | 17 | 3753.6 | 71277.3018
1412-Forced draft fan drives (other than motor) | 59 | 58 | 12148.6 | 276790.9288
1413-Forced draft fan couplings | 7 | 7 | 1180.4 | 30175.5899
1415-Forced draft fan controls | 85 | 85 | 15264.5 | 176435.3841
1420-Other forced draft fan problems | 171 | 171 | 15788.08 | 823063.8962
1421-Secondary air fans/blowers | 24 | 24 | 3580.56 | 25873.4524
1422-Secondary air fan/blower motors - single speed | 1 | 1 | 18 | 114
1423-Secondary air fan/blower motors - variable speed | 2 | 2 | 74.13 | 416.1688
1424-Secondary air fan/blower controls | 6 | 6 | 1242.76 | 2296.8767
1430-Air supply ducts from FD fan | 39 | 39 | 2735.16 | 356585.8607
1431-Air supply dampers from FD fan | 37 | 36 | 1641.85 | 272307.4164
1432-Air supply duct expansion joints | 9 | 9 | 1894.38 | 163795.0588
1440-Air supply dampers | 33 | 33 | 3045.33 | 57526.6939
1450-Other air supply problems | 104 | 104 | 10232.06 | 253776.9395
1455-Induced draft fans | 1319 | 1292 | 68624.99 | 2150832.435
1456-Induced draft fan dampers | 50 | 50 | 4626.2 | 70398.1019
1457-Induced draft fan lubrication systems | 52 | 52 | 10366.81 | 255690.6333
1460-Induced draft fan fouling | 64 | 64 | 7247.31 | 79238.7256
1470-Induced draft fan motors and drives | 180 | 180 | 26897.96 | 860350.0727
1471-Induced draft fan motors - variable speed | 83 | 83 | 18583.86 | 237456.891
1472-Inducted draft fan coupling | 5 | 5 | 753 | 29580.7499
1475-Induced draft fan controls | 193 | 193 | 34337.42 | 566860.0921
1476-Induced draft fan speed changer | 14 | 14 | 2813.47 | 16560.1728
1480-Other induced draft fan problems | 448 | 439 | 38738.41 | 1072104.5969
1487-Air heater (tubular) | 19 | 19 | 1838.19 | 471325.7982
1488-Air heater (regenerative) | 613 | 607 | 55992.64 | 2797528.0761
1489-Air heater (heat pipe; plate-type) | 8 | 8 | 1539.3 | 35910.816
1492-Air heater fouling (tubular) | 9 | 9 | 208 | 6669.6616
1493-Air heater fouling (regenerative) | 840 | 776 | 17104.75 | 1460480.3683
1495-Other air heater fouling (heat pipe; plate-type) | 10 | 10 | 272.01 | 13542.8138
1500-Air heater soot blowers | 6 | 6 | 633.07 | 1270.5848
1510-Flue gas ducts (except recirculation) | 121 | 119 | 5209.28 | 343463.137
1512-Flue gas expansion joints | 60 | 60 | 6531.18 | 281699.4366
1520-Flue gas dampers (except recirculation) | 8 | 8 | 1010.85 | 37760.4429
1530-Other flue gas problems | 154 | 105 | 5019.9 | 79480.5062
1535-Flue gas recirculating fan | 17 | 17 | 2641 | 46381.1828
1536-Flue gas recirculating fan dampers | 1 | 1 | 135 | 85.5
1537-Flue gas recirculating fan lubrication systems | 1 | 1 | 161 | 407.8666
1550-Flue gas recirculation fan motors | 9 | 9 | 2098 | 45846.8655
1555-Flue gas recirculation fan controls | 1 | 1 | 500 | 8933.333
1560-Other flue gas recirculation fan problems | 1 | 1 | 569 | 9388.5
1572-Flue gas recirculation duct expansion joints | 1 | 1 | 32 | 41.0667
1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | 6 | 6 | 1295 | 10382.3328
1591-Stack damper and linkage | 16 | 16 | 2673.75 | 8918.9748
1599-Other miscellaneous boiler air and gas system problems | 153 | 153 | 10572.61 | 241634.3152
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 224 | 223 | 60203.15 | 341998.2692
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 178 | 178 | 32964.62 | 486736.6947
1720-Desuperheater/attemperator controls | 48 | 48 | 6851.32 | 144441.1804
1730-Boiler explosion or implosion | 1 | 1 | 82 | 45757.3666
1740-Boiler drum gage glasses/level indicator | 69 | 69 | 18337.67 | 103961.9676
1741-Furnace and water gauge television auxiliary system | 7 | 7 | 740 | 1354.1664
1750-Burner management system | 162 | 161 | 35028.32 | 521812.9273
1760-Feedwater instrumentation (not local controls) | 26 | 26 | 6746.4 | 22469.3518
1761-Combustion /Steam condition instrumentation (not local controls) | 22 | 22 | 6419.6 | 31204.3608
1762-Desuperheater/attemperator instrumentation (not local controls) | 3 | 3 | 399 | 1888.2499
1799-Other boiler instrumentation and control problems | 357 | 357 | 59046.45 | 534223.5395
1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | 12 | 12 | 3483.92 | 279010.0694
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 11 | 11 | 1006.2 | 75527.1512
1810-Other boiler inspections | 7 | 7 | 609.61 | 84870.5398
1811-Boiler Inspections - problem identification/investigative | 4 | 4 | 468 | 10465.733
1812-Boiler Inspections - scheduled or routine | 7 | 7 | 694 | 3539.6
1850-Boiler water condition (not feedwater water quality) | 621 | 620 | 85204.75 | 1267863.3374
1900-Improper balance between tube sections not due to fouling or plugging | 14 | 14 | 390 | 3398.3499
1910-Inadequate air not due to equipment problems | 6 | 6 | 221 | 12028.9667
1980-Boiler safety valve test | 15 | 15 | 1884.62 | 30806.6928
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 40 | 39 | 4966.67 | 40883.1182
1999-Boiler; miscellaneous | 784 | 776 | 42186.14 | 4102983.8705
2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | 2 | 2 | 120.76 | 23236.0703
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 10 | 10 | 797.88 | 5337.4886
2030-Fuel limits - peaking factors | 1 | 1 | 790.57 | 3623.4456
2033-Fuel limits - MAPLHGR (Maximum Average Planar Linear Heat Generation Rate - BWR units only) | 1 | 1 | 10 | 35
2040-Core physics tests | 3 | 3 | 296.91 | 18994.4767
2060-Excore nuclear instrumentation | 1 | 1 | 3 | 436.85
2061-Incore nuclear instrumentation | 1 | 1 | 3 | 3
2082-Fuel transfer problems (CANDU) | 3 | 3 | 1001.91 | 516425.8113
2090-Other core/fuel problems | 1 | 1 | 28 | 371
2110-Control rod drive motors | 1 | 1 | 297.94 | 23929.5475
2112-Control rod hydraulic drives | 1 | 1 | 282.54 | 720.477
2120-Control rod scram mechanisms | 3 | 3 | 92.76 | 290.1899
2130-Control rod assemblies other than drive and scram mechanisms | 2 | 2 | 1792.2 | 110661.0988
2150-Control rod instrumentation | 1 | 1 | 3.1 | 33.5833
2151-Control rod drive controls | 2 | 2 | 2200 | 143053.1656
2152-Control rod drive power supplies | 1 | 1 | 162.97 | 2020.828
2160-Other control rod drive problems | 20 | 20 | 7367.89 | 77361.6867
2170-Reactor vessel flanges and seals | 20 | 19 | 4970 | 117703
2176-Control rod guides (not in fuel) | 1 | 1 | 928 | 46400
2199-Other reactor vessel problems | 1 | 1 | 1150 | 21811.6659
2200-Reactor coolant/recirculating pumps | 7 | 7 | 1854.43 | 124201.0212
2210-Reactor coolant/recirculating pump motors | 16 | 16 | 8408.12 | 144086.8048
2230-Reactor coolant system piping | 1 | 1 | 946.2 | 9698.55
2270-Power operated relief and safety/relief valves | 1 | 1 | 128 | 4354.1332
2290-Pressurizer spray valves | 5 | 5 | 3420 | 270584.6658
2340-Pressurizer pressure instruments and controls | 1 | 1 | 16.18 | 16.7193
2350-BWR feedwater controls | 2 | 2 | 19 | 167
2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | 3 | 3 | 146.67 | 524.9688
2380-Reactor control system/integrated control system problems | 6 | 6 | 1846 | 69156.9154
2399-Other miscellaneous reactor coolant system problems | 4 | 4 | 1855.45 | 108952.613
2420-Steam generator moisture separators and dryers | 2 | 2 | 1380 | 81489.9992
2421-Steam generator feedwater nozzles | 1 | 1 | 12 | 159
2440-Steam generator chemistry (excluding feedwater chemistry) | 8 | 8 | 833.17 | 16724.4263
2460-Blowdown system valves B | 25 | 25 | 1131.91 | 307012.025
2480-Other blowdown | 19 | 19 | 380.74 | 250310.0073
2510-Main steam isolation valves (BWR and PWR) | 13 | 13 | 9689.96 | 743200.8119
2515-Main steam isolation valve testing | 1 | 1 | 30 | 6
2521-Main steam safety/relief valve testing | 1 | 1 | 0 | 0
2540-Other steam valves | 11 | 11 | 251.64 | 183998.64
2599-Other steam generator problems | 2 | 2 | 1421.85 | 70603.25
2620-Low pressure safety injection; core spray; or decay heat pumps | 1 | 1 | 300 | 2319.9999
2623-Low pressure valves | 1 | 1 | 108 | 1836
2625-Accumulators (up to and including check valves) | 3 | 3 | 1701.15 | 234706.5384
2628-Residual heat removal/decay heat removal system | 1 | 1 | 1122 | 54061.6996
2649-Other emergency core cooling/residual heat removal system problems | 4 | 4 | 3534.8 | 214285.2556
2650-Emergency diesel generators (including actuating systems) | 1 | 1 | 1006 | 121340.366
2660-Safeguard buses and associated equipment (transformers; breakers; etc.) | 1 | 1 | 967 | 137249.533
2680-120V AC safety system power supplies (including inverter) | 1 | 1 | 685 | 132342
2700-Containment structure | 2 | 2 | 1342.86 | 106466.4166
2720-Containment isolation valves and dampers | 1 | 1 | 9 | 99
2810-Makeup pumps | 1 | 1 | 42.91 | 195.9556
2817-Instruments and controls | 1 | 1 | 354.5 | 4254
2819-Other CVCS and RWC problems | 3 | 3 | 190.36 | 2096.096
2829-Other closed cooling water system problems B | 1 | 1 | 1161 | 452383.65
2831-Nuclear service water piping | 4 | 4 | 720 | 4485.7497
2844-Auxiliary feedwater valves | 1 | 1 | 0 | 0
2999-Other miscellaneous nuclear reactor problems | 1 | 1 | 1282 | 212812
3110-Condenser tube leaks | 368 | 368 | 92591.18 | 3250152.0682
3111-Condenser tube fouling shell side | 12 | 12 | 921 | 8464.9498
3112-Condenser tube fouling tube side | 381 | 378 | 18251.29 | 546389.6788
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 245 | 237 | 37984.61 | 311442.0483
3114-Air-cooled condenser tubes | 5 | 5 | 330.4 | 6733.5132
3115-Air-cooled condenser pumps | 2 | 2 | 131.28 | 137.3253
3116-Air-cooled condenser fans | 2 | 2 | 99.3 | 40.94
3118-Other Air-cooled condenser problems | 35 | 35 | 2108.2 | 9260.9895
3119-Other condenser tube casing or shell and internal problems | 7 | 7 | 938.18 | 22744.6139
3120-Tube sheets | 4 | 4 | 372 | 2368.9998
3121-Expansion joint | 14 | 14 | 2126.76 | 110177.3259
3122-Gaskets and seals | 21 | 21 | 3943.8 | 358408.4858
3123-Hot well | 17 | 17 | 1787.57 | 69751.5724
3124-Tube sheet fouling | 18 | 18 | 1953.62 | 17732.9904
3129-Other condenser casing or shell and internal problems | 6 | 6 | 714 | 19999.3832
3130-Air ejectors | 22 | 22 | 1815.55 | 13763.277
3131-Air ejector piping and valves | 18 | 18 | 2743.69 | 29958.0843
3132-Inter and after condensers | 1 | 1 | 47.7 | 302.1
3133-Vacuum pumps | 43 | 43 | 6526.86 | 50398.8785
3134-Vacuum pump piping and valves | 13 | 13 | 2277.36 | 7056.3182
3135-Vacuum pump motor and auxiliaries | 6 | 6 | 1034 | 4543.633
3139-Other air extraction system problems - general | 17 | 17 | 1774.2 | 3107.301
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 335 | 334 | 40826.86 | 690862.9455
3150-Hot well level controls | 27 | 27 | 4576.6 | 33522.6502
3151-Vacuum pump and air ejector controls | 10 | 10 | 2124.7 | 24619.5245
3152-Air-cooled condenser controls | 1 | 1 | 11 | 0.91666
3159-Other condensing system controls and instruments | 22 | 22 | 3670.68 | 90569.3535
3170-Condenser inspection (use code 3110 to report looking for tube leaks) | 2 | 2 | 393 | 3054.7499
3186-Auxiliary Condenser and Associated Equipment | 19 | 19 | 2527.46 | 9158.756
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 21 | 21 | 3888.69 | 81194.3117
3199-Other miscellaneous condensing system problems | 76 | 76 | 7839.2 | 181853.6205
3210-Circulating water pumps | 284 | 284 | 41365.28 | 2461556.4508
3211-Circulating water pump motors | 167 | 153 | 17364.36 | 852311.2209
3220-Circulating water piping | 54 | 54 | 10011.95 | 1501819.4523
3221-Circulating water piping fouling | 12 | 12 | 1745.6 | 36291.1498
3230-Circulating water valves | 49 | 49 | 4622.33 | 98363.3777
3231-Waterbox | 12 | 12 | 2160 | 28287.4993
3232-Condenser tube cleaning system including debris filter | 18 | 18 | 2786.6 | 88925.4253
3233-Circulating water priming system | 1 | 1 | 4 | 68
3235-Cooling tower booster pump | 3 | 3 | 513 | 97318.1332
3238-Cooling tower fan motors | 19 | 19 | 1447.8 | 39727.4396
3239-Cooling tower fan motors - variable speed | 14 | 14 | 1191.5 | 11703.1831
3240-Cooling tower fans | 39 | 39 | 3346.7 | 58443.402
3241-Cooling tower efficiency below design | 102 | 100 | 3343.3 | 32657.2008
3242-Cooling tower fill damage | 1 | 1 | 54 | 30140.1
3243-Cooling tower icing | 9 | 9 | 290.8 | 14313.7266
3244-Cooling tower fires | 1 | 1 | 339 | 42075.5498
3245-Other cooling tower problems | 72 | 72 | 8640.12 | 1601822.4858
3246-Cooling tower fouling | 8 | 6 | 175 | 22310.5667
3247-Cooling tower instrumentation | 14 | 14 | 2593 | 23032.8657
3250-Circulating water system instruments and controls | 38 | 38 | 5576.37 | 23126.751
3260-Traveling screens | 59 | 59 | 6614.07 | 250118.0474
3261-Traveling screen fouling | 29 | 29 | 3909.05 | 25665.8806
3269-Circulating water biological conditions (ie; zebra mussels) | 7 | 7 | 2000.9 | 21969.1845
3270-Intake system problems other than traveling screens | 28 | 28 | 3163.95 | 156623.944
3271-Intake grating fouling | 28 | 28 | 3827.36 | 35807.6399
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 28 | 28 | 2144.7 | 78501.296
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 27 | 19 | 4581 | 39070.4822
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 148 | 147 | 5039.14 | 91681.451
3281-Circulating water tempering system | 1 | 1 | 29.27 | 24.8795
3282-Circulating water cooling ponds | 2 | 2 | 508 | 36049.3831
3285-Circulating water chemistry | 11 | 11 | 742.7 | 7203.8698
3290-Waste water (zero discharge) tanks; pumps and motors | 2 | 2 | 63 | 221
3291-Waste water (zero discharge) system fouling | 1 | 1 | 59 | 93.4166
3299-Other circulating water system problems | 41 | 39 | 4416.92 | 1261707.5097
3300-Condensate water pre-treatment | 3 | 3 | 1091 | 17919.9829
3310-Condensate/hotwell pumps | 190 | 190 | 32058.87 | 1078597.405
3311-Condensate/hotwell pump motor | 82 | 82 | 12051.52 | 453517.2836
3312-Condensate booster pump | 18 | 18 | 3819.72 | 90826.8966
3313-Condensate booster pump motor | 7 | 7 | 680.3 | 50855.4582
3314-Condensate booster pump motor - variable speed | 3 | 3 | 1210 | 11834.4996
3320-Condensate piping | 33 | 33 | 7767.69 | 724744.0885
3330-Condensate valves | 37 | 37 | 7912.55 | 48718.2385
3339-LP heater head leaks | 1 | 1 | 175 | 17243.3333
3340-LP heater tube leaks | 16 | 16 | 2816.2 | 231710.152
3341-Other LP heater - general | 47 | 45 | 4302.71 | 131268.1518
3342-IP heater tube leaks | 20 | 20 | 2553 | 380266.1493
3343-Other IP heater - general | 12 | 12 | 1395.39 | 74514.7603
3344-Deaerator (including level control) | 68 | 68 | 12630.34 | 282337.7083
3350-Condensate polishing and filtering systems | 49 | 49 | 8215.41 | 51237.6088
3351-Chemical addition systems | 2 | 2 | 262 | 4556.6166
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 179 | 179 | 27829.11 | 455239.8917
3360-Condensate makeup and return (including storage tanks) | 26 | 26 | 2833.58 | 36446.5045
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 27 | 27 | 3953.9 | 30535.8791
3380-Condensate coolers | 5 | 5 | 334.14 | 23000.5066
3399-Other miscellaneous condensate system problems | 42 | 42 | 7045.21 | 88314.5924
3401-Startup feedwater pump | 22 | 22 | 5705.26 | 113610.664
3402-Startup feedwater pump drives - all types | 1 | 1 | 500 | 8758.333
3407-Feedwater pump suction screens | 6 | 6 | 1343.7 | 11094.706
3408-Feedwater pump drive - local controls | 64 | 64 | 17774.82 | 239495.1737
3409-Feedwater pump drive motor - variable speed | 8 | 8 | 605.46 | 83792.4925
3410-Feedwater pump | 734 | 570 | 109268.43 | 5344501.2964
3411-Feedwater pump drive - motor | 128 | 128 | 14727.37 | 1313492.5634
3412-Feedwater pump drive - steam turbine | 193 | 193 | 53573.96 | 1317595.6615
3413-Feedwater pump coupling and drive shaft | 20 | 20 | 3815.36 | 126920.4102
3414-Feedwater pump local controls | 74 | 74 | 17397.48 | 235806.0472
3415-Feedwater pump/drive lube oil system | 110 | 110 | 24385.34 | 428825.8397
3416-Other feedwater pump problems | 173 | 173 | 36969.17 | 1026360.8918
3417-Feedwater pump drive - main shaft | 6 | 6 | 2089 | 172663.0163
3418-Feedwater pump drive - other | 24 | 24 | 4186.85 | 96827.9111
3419-Feedwater pump drive - gear | 12 | 12 | 1245 | 269614.4994
3420-Feedwater piping and supports | 48 | 48 | 12590.54 | 246493.6666
3430-Feedwater regulating (boiler level control) valve | 169 | 169 | 35231.63 | 719407.6047
3431-Other feedwater valves | 171 | 171 | 37270.15 | 1284126.4995
3439-HP heater head leaks | 38 | 38 | 7039.54 | 339509.1823
3440-High pressure heater tube leaks | 183 | 182 | 13003.23 | 1234571.5554
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 131 | 131 | 16169.56 | 433718.0048
3451-Feedwater Booster Pump Suction Screens | 1 | 1 | 370 | 6123.5
3452-Feedwater Booster Pump Drive - Local Controls | 1 | 1 | 97 | 714.5666
3454-Feedwater Booster Pump | 9 | 9 | 1421.91 | 58502.7088
3455-Feedwater Booster Pump Drive - Motor | 2 | 2 | 1051 | 28040.9997
3456-Feedwater Booster Pump Drive - Steam Turbine | 4 | 4 | 365.74 | 4155.9609
3458-Feedwater Booster Pump Local Controls | 2 | 2 | 617 | 840.5
3459-Feedwater Booster Pump/Drive Lube Oil System | 4 | 4 | 821 | 7432.283
3460-Other Feedwater Booster Pump Problems | 11 | 11 | 2904.1 | 90301.1623
3461-Feedwater Booster Pump Drive - Main Shaft | 1 | 1 | 10.83 | 64.98
3499-Other feedwater system problems | 148 | 148 | 28733.96 | 342039.7758
3501-Heater drain pumps | 31 | 31 | 2818.92 | 71406.7456
3502-Heater level control | 74 | 74 | 8844.37 | 415628.3898
3503-Heater drain piping | 57 | 56 | 1524.5 | 47524.391
3504-Heater drain valves | 59 | 58 | 4933.74 | 299983.5469
3505-Heater drain pump drive | 2 | 2 | 35 | 242.0833
3509-Other heater drain system problems | 16 | 16 | 910.33 | 12148.609
3520-HP Extraction steam piping | 15 | 15 | 5619 | 73150.6319
3521-HP Extraction steam valves | 54 | 54 | 5273.33 | 136818.5818
3522-HP Extraction steam instruments and controls | 1 | 1 | 47 | 520.1333
3529-Other HP extraction steam system problems | 5 | 5 | 1633 | 22484.416
3530-IP Extraction steam piping | 2 | 2 | 249 | 4856.9999
3531-IP Extraction steam valves | 10 | 10 | 2302.97 | 121026.2869
3532-IP Extraction steam instruments and controls | 7 | 7 | 1268 | 12473.2827
3539-Other IP extraction steam system problems | 1 | 1 | 230 | 276
3540-LP Extraction steam piping | 2 | 2 | 36 | 5288
3541-LP Extraction steam valves | 6 | 6 | 1885 | 29070.9161
3549-Other LP extraction steam system problems | 1 | 1 | 635 | 1576.9165
3600-Switchyard transformers and associated cooling systems - external | 52 | 52 | 4604.87 | 544184.7277
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 9 | 9 | 487.1 | 2618.2415
3610-Switchyard circuit breakers - (not outside management control) | 53 | 53 | 5919.08 | 114518.4099
3611-Switchyard circuit breakers - external | 170 | 170 | 19210.49 | 1059838.3247
3612-Switchyard system protection devices - external | 172 | 172 | 18771.41 | 504832.0136
3613-Switchyard system protection devices - (not outside management control) | 57 | 57 | 5882.6 | 65949.9782
3618-Other switchyard equipment ? (not outside management control) | 13 | 13 | 3462.16 | 136760.1803
3619-Other switchyard equipment - external | 186 | 186 | 22454.62 | 1789167.0249
3620-Main transformer | 466 | 466 | 65844.15 | 14955198.916
3621-Unit auxiliaries transformer | 135 | 135 | 18160.67 | 1211406.2314
3622-Station service startup transformer | 48 | 48 | 10708.07 | 678967.4659
3623-Auxiliary generators | 4 | 4 | 137.57 | 6148.282
3624-Generator Voltage Supply System | 30 | 30 | 2926.66 | 129745.1087
3629-Other switchyard or high voltage system problems - external | 94 | 94 | 11527.19 | 2077587.6123
3630-480-volt transformers | 17 | 17 | 1757.95 | 55054.6476
3631-480-volt circuit breakers | 137 | 136 | 23474.81 | 340619.0292
3632-480-volt conductors and buses | 39 | 38 | 10133.57 | 76451.7582
3633-480-volt insulators | 2 | 2 | 520 | 7865
3634-480-volt protection devices | 9 | 9 | 1380.82 | 9466.1864
3639-Other 480-volt problems | 19 | 19 | 2983.71 | 13880.2695
3640-AC instrument power transformers | 11 | 11 | 761.75 | 36354.3697
3641-AC Circuit breakers | 66 | 66 | 8015.11 | 314125.622
3642-AC Conductors and buses | 56 | 56 | 10790.16 | 1645183.6783
3643-AC Inverters | 20 | 20 | 5030.14 | 228458.3285
3644-AC Protection devices | 166 | 166 | 18412.16 | 2076317.8179
3649-Other AC instrument power problems | 40 | 40 | 4092.93 | 90941.1944
3650-DC instrument power battery chargers | 29 | 29 | 2539.61 | 85588.4762
3651-DC circuit breakers | 6 | 6 | 534.1 | 10230.4414
3652-DC conductors and buses | 9 | 9 | 625 | 74767.3665
3653-DC protection devices | 20 | 20 | 1204.38 | 12595.8645
3659-Other DC power problems | 41 | 41 | 5427.27 | 341690.4883
3660-4160-volt transformers | 14 | 14 | 3341.16 | 138086.7315
3661-4160-volt circuit breakers | 116 | 116 | 24647.77 | 283848.0183
3662-4160-volt conductors and buses | 57 | 57 | 14294.38 | 690464.4011
3663-4160-volt insulators | 1 | 1 | 151 | 2642.5
3664-4160-volt protection devices | 37 | 37 | 7744.3 | 72608.7569
3669-Other 4160-volt problems | 17 | 17 | 2719.5 | 21405.9496
3670-12kV transformers | 10 | 10 | 1568.58 | 39202.3553
3671-12kV circuit breakers | 51 | 51 | 8249.59 | 378544.4991
3672-12kV conductors and buses | 53 | 53 | 7039.68 | 747043.085
3673-12kV insulators | 2 | 2 | 170.75 | 9356.5457
3674-12kV protection devices | 21 | 21 | 1999.54 | 181433.4203
3679-Other 12kV problems | 16 | 16 | 2059.54 | 70091.1539
3680-Other voltage system transformers | 20 | 20 | 3061.32 | 175319.9397
3681-Other voltage system breakers | 50 | 50 | 5441.92 | 38254.654
3682-Other voltage system conductors and buses | 9 | 9 | 1608.4 | 69758.6658
3683-Other voltage system insulators | 8 | 8 | 1162.8 | 26607.4111
3684-Other voltage system protection devices | 91 | 90 | 10882.83 | 234150.128
3689-Other Other voltage system problems | 57 | 57 | 3935.46 | 125366.7471
3690-Station Service Power Distribution System; General | 48 | 48 | 6627.64 | 148678.6924
3700-Power Station switchyard (non generating unit equipment) | 24 | 24 | 3068.57 | 91580.6335
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 108 | 108 | 9186.89 | 294233.9853
3720-Transmission equipment at the 1st substation) | 36 | 36 | 2730.87 | 80793.8451
3730-Transmission equipment beyond the 1st substation | 87 | 87 | 9411.5 | 150923.2068
3800-Open cooling water pumps and motors | 8 | 8 | 773 | 8340.5164
3801-Open cooling water piping | 2 | 2 | 60 | 5877.5333
3802-Open cooling water valves | 1 | 1 | 106.94 | 76.6403
3803-Open cooling water heat exchangers | 6 | 6 | 926 | 6473.6497
3804-Open cooling water system fouling | 1 | 1 | 200 | 12973.3332
3809-Other open cooling water problems | 2 | 2 | 1022 | 10871.9166
3810-Service water pumps and motors | 20 | 20 | 3027.05 | 199402.6847
3811-Service water piping | 49 | 49 | 12627.16 | 217826.4142
3812-Service water valves | 7 | 7 | 668.28 | 8359.8496
3813-Service water heat exchangers | 3 | 3 | 328 | 19171.4166
3814-Service water system fouling | 5 | 5 | 318.15 | 3674.655
3815-Service water strainer | 1 | 1 | 7 | 7
3819-Other service water problems A | 40 | 40 | 5643.32 | 136831.4515
3820-Closed cooling water pumps | 18 | 18 | 1348.33 | 62942.9465
3821-Closed cooling water piping | 29 | 29 | 2056.73 | 92854.2805
3822-Closed cooling water valves | 5 | 5 | 1172.1 | 8419.6165
3823-Closed cooling water heat exchangers | 25 | 25 | 4776.22 | 464937.7915
3824-Closed cooling water system fouling | 7 | 7 | 482.72 | 11900.4689
3825-Closed cooling water instrumentation | 1 | 1 | 74.97 | 443.5725
3826-Closed cooling water strainer | 1 | 1 | 71 | 5235.0666
3829-Other closed cooling water system problems A | 51 | 51 | 4995 | 59007.6202
3830-Auxiliary boiler | 30 | 30 | 10988.83 | 216244.7144
3831-Auxiliary steam piping | 23 | 23 | 6715.2 | 193935.356
3832-Auxiliary steam valves | 29 | 29 | 5494.32 | 97661.9914
3833-Auxiliary steam controls and instruments | 16 | 16 | 3275.68 | 11114.4196
3834-Auxiliary boiler tube leaks | 6 | 6 | 1320.3 | 284789.4281
3835-Auxiliary boiler burner management system | 2 | 2 | 265 | 1026.1832
3836-Steam Transfer to Other Unit | 179 | 175 | 8603.09 | 94146.2226
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 24 | 24 | 4864.36 | 39183.5627
3840-Service air compressors | 37 | 35 | 3284.2 | 14547.7521
3842-Service air valves | 4 | 4 | 908 | 11757.5663
3843-Service air dryers | 12 | 12 | 955.66 | 1057.0701
3844-Soot blowing air compressor and system | 35 | 35 | 5178.9 | 48232.5148
3849-Other service air problems | 10 | 10 | 757.75 | 16601.2538
3850-Instrument air compressors | 80 | 80 | 10035.37 | 54216.041
3851-Instrument air piping | 21 | 21 | 3233.93 | 7979.374
3852-Instrument air valves | 7 | 7 | 1680.94 | 268360.8457
3853-Instrument air dryers | 5 | 5 | 199.41 | 622.78
3854-N2 backup to instrument air | 1 | 1 | 15 | 14.75
3859-Other instrument air problems | 30 | 30 | 6457.4 | 136058.343
3860-Fire protection system pumps | 8 | 8 | 359.7 | 8097.0063
3861-Fire protection system piping | 11 | 11 | 1386 | 12072.0997
3862-Fire protection system valves | 13 | 13 | 831.18 | 7919.2871
3864-Fire protection system instrumentation and controls | 49 | 49 | 3684.65 | 103670.4609
3869-Other fire protection system problems | 71 | 71 | 6124.28 | 208685.7315
3870-Fuel Gas Compressor and Motors | 74 | 73 | 3493.4 | 119362.8192
3871-Fuel Gas Compressor Piping | 16 | 16 | 1183.6 | 12370.3931
3872-Fuel Gas Compressor Valves | 47 | 47 | 2735.75 | 7382.5729
3873-Fuel Gas Compressor Heat Exchangers | 5 | 5 | 526.9 | 25074.82
3874-Fuel Gas Compressor Controls and Instrumentation | 87 | 86 | 5315.15 | 40858.3027
3875-Fuel Gas Compressor Filters | 3 | 3 | 142.2 | 560.47
3879-Fuel Gas Compressor - other | 64 | 63 | 3134.22 | 8099.2748
3881-Seal air fan drive - motor | 1 | 1 | 78 | 310.7
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 83 | 83 | 6449.18 | 80676.5105
3899-Other miscellaneous auxiliary system problems | 113 | 113 | 10165.69 | 414968.9157
3950-Process computer | 71 | 71 | 6843.54 | 124804.7794
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 192 | 191 | 3711.76 | 795511.4257
3970-Distributive Control System (DCS) - process computer | 74 | 74 | 8912.68 | 162338.1964
3971-DCS - data highway | 36 | 36 | 3890.35 | 70246.0073
3972-DCS - hardware problems (including card failure) | 123 | 123 | 16011.46 | 250276.5935
3973-DCS - internal and termination wiring | 19 | 19 | 3813.81 | 46276.4125
3974-DCS - logic problems | 87 | 86 | 15066.84 | 75032.037
3975-DCS - upgrades | 36 | 35 | 10364.5 | 170839.3216
3979-Other DCS problems | 84 | 83 | 15159.95 | 142808.4873
3980-Programmable Logic Controller (PLC) | 27 | 27 | 2012.09 | 63344.9306
3981-PLC - data highway | 9 | 9 | 1281.74 | 12486.2124
3982-PLC - hardware problems (including card failure) | 33 | 33 | 3594.87 | 64355.1889
3983-PLC - internal and termination wiring | 1 | 1 | 133 | 399
3984-PLC - logic problems | 12 | 12 | 870.21 | 3516.9999
3985-PLC - upgrades | 3 | 3 | 350.1 | 738.4583
3989-Other PLC problems | 14 | 14 | 665.46 | 8704.1263
3995-Powerhouse heating and ventilating systems | 3 | 3 | 104 | 51.3333
3996-Air conditioning systems - rooms and areas | 3 | 3 | 220 | 10666.5332
3998-Balance of plant overhaul/outage | 1 | 1 | 69.6 | 400.2
3999-Other miscellaneous balance of plant problems | 380 | 379 | 37043.28 | 616963.0508
4000-Outer casing A | 4 | 4 | 357 | 297101.8166
4001-Inner casing C | 1 | 1 | 839 | 173435.2828
4010-Nozzles and nozzle blocks C | 2 | 2 | 14 | 3539
4011-Diaphragms A | 35 | 33 | 883.1 | 252469.1298
4012-Buckets or blades A | 2 | 2 | 106.88 | 217616.2466
4014-Bucket or blade fouling C | 594 | 468 | 5081.25 | 709599.6774
4020-Shaft seals B | 9 | 9 | 1334.8 | 16431.5829
4022-Gland rings C | 9 | 9 | 123.7 | 1355.7783
4030-Rotor shaft C | 15 | 14 | 1860 | 908351.6161
4040-Bearings C | 159 | 159 | 18038.06 | 734054.5017
4041-HP steam turbine thrust bearings | 22 | 22 | 3891.79 | 312477.1302
4099-Other high pressure turbine problems | 535 | 500 | 23356.31 | 3345527.6691
4100-Outer casing B | 2 | 2 | 469.2 | 21037.56
4101-Inner casing B | 1 | 1 | 73 | 188.5833
4120-Shaft seals C | 3 | 3 | 210 | 414.5
4130-Rotor shaft B | 5 | 5 | 3590 | 168837.7
4140-Bearings D | 18 | 18 | 6619.1 | 415175.8413
4141-IP steam turbine thrust bearings | 3 | 3 | 600 | 21998.3996
4199-Other intermediate pressure turbine problems | 40 | 40 | 13506.4 | 741192.2685
4201-Inner casing A | 1 | 1 | 658 | 39611.6
4211-Diaphragms C | 3 | 3 | 843 | 3330.1161
4212-Buckets or blades C | 15 | 15 | 1690.34 | 814441.7111
4213-Bucket or blade fouling A | 7 | 4 | 56 | 683.2
4220-Shaft seals D | 1 | 1 | 32 | 96
4230-Rotor shaft A | 6 | 6 | 2166 | 802895.1654
4240-Bearings E | 60 | 60 | 12968.05 | 1837726.6632
4241-LP steam turbine thrust bearings | 7 | 7 | 966 | 194512.0665
4250-Other low pressure turbine problems | 46 | 46 | 5996.48 | 936706.619
4260-Main stop valves | 155 | 155 | 28044.8 | 1050761.652
4261-Control valves | 507 | 502 | 83376.02 | 3081582.7191
4262-Intercept valves | 81 | 81 | 19087.06 | 636839.3186
4263-Reheat stop valves | 55 | 55 | 13453.1 | 686237.6498
4264-Combined intercept valves | 10 | 10 | 2592.27 | 202935.8165
4265-Miscellaneous drain and vent valves | 24 | 24 | 5613.7 | 94907.594
4266-Main stop valve testing | 34 | 34 | 7986.22 | 74288.7462
4267-Control valve testing | 38 | 38 | 6263.63 | 32907.3816
4268-Reheat/intercept valve testing | 13 | 13 | 4544.5 | 43313.9567
4269-Other turbine valves (including LP steam admission valves) | 99 | 98 | 19152.38 | 806173.361
4270-Crossover or under piping | 25 | 25 | 10440 | 419203.6628
4279-Miscellaneous turbine piping | 51 | 51 | 11045.38 | 465536.7882
4280-Lube oil pumps A | 20 | 20 | 3663.2 | 81118.2991
4281-Lube oil coolers A | 26 | 26 | 6843.74 | 613155.5475
4282-Lube oil conditioners | 3 | 3 | 435 | 9917.3333
4283-Lube oil system valves and piping | 23 | 23 | 3941.48 | 56764.667
4284-Lube oil pump drive | 11 | 11 | 3180.82 | 129710.3019
4289-Other lube oil system problems | 87 | 87 | 15747.68 | 801627.7521
4290-Hydraulic system pumps | 28 | 28 | 7382.43 | 111158.308
4291-Hydraulic system coolers | 5 | 5 | 1503 | 23651.4826
4292-Hydraulic system filters | 7 | 7 | 2861 | 17403.3156
4293-Hydraulic system pipes and valves | 116 | 116 | 33213.37 | 413167.7935
4299-Other hydraulic system problems | 74 | 74 | 17914.91 | 287194.6625
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 100 | 99 | 24680.44 | 1716781.9934
4301-Turbine governing system | 124 | 124 | 19632.94 | 602948.8408
4302-Turbine trip devices (including instruments) | 217 | 217 | 44470.97 | 1081289.9817
4303-Exhaust hood and spray controls | 16 | 16 | 4910.85 | 42989.2776
4304-Automatic turbine control systems - mechanical | 13 | 13 | 2643 | 81764.3074
4305-Automatic turbine control systems - mechanical - hydraulic | 29 | 29 | 6406.66 | 132202.4221
4306-Automatic turbine control systems - electro-hydraulic - analog | 13 | 13 | 2277.07 | 42083.5192
4307-Automatic turbine control systems - electro-hydraulic - digital | 24 | 24 | 5135.1 | 47788.0247
4308-Automatic turbine control systems - digital control and monitoring | 87 | 87 | 21930.41 | 221364.8488
4309-Other turbine instrument and control problems | 114 | 114 | 21315.77 | 360461.0007
4310-Steam Turbine Control System - data highway | 12 | 12 | 1926.6 | 21284.5892
4311-Steam Turbine Control System - hardware problems (including card failure) | 84 | 84 | 23652.58 | 272153.0738
4312-Steam Turbine Control System - internal and termination wiring | 7 | 7 | 1816.2 | 27347.6894
4313-Steam Turbine Control System - logic problems | 43 | 43 | 7491.33 | 1081738.8441
4314-Steam Turbine Control System - upgrades | 3 | 3 | 775 | 4734.4997
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 9 | 9 | 1301.87 | 2213094.9795
4401-Inspection F | 1 | 1 | 727 | 338333.6831
4410-Turning gear and motor A | 42 | 42 | 6437.6 | 281798.2819
4411-Steam turbine gear box (single shaft configuration) | 2 | 2 | 57 | 180.6166
4415-Shaft coupling mechanism | 6 | 6 | 1167.3 | 152500.1913
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 253 | 253 | 56924.92 | 3112518.4248
4430-Gland seal system | 54 | 54 | 8536.22 | 97116.5466
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 22 | 22 | 1380.95 | 97840.6112
4445-Steam reheater | 16 | 16 | 2535.67 | 374121.8556
4450-Water induction | 9 | 9 | 3141.7 | 1611448.4428
4460-Turbine overspeed trip test | 13 | 13 | 1243.88 | 22223.3995
4470-Differential expansion | 99 | 98 | 24139.81 | 539951.9874
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 10 | 10 | 1991.88 | 65620.7823
4499-Other miscellaneous steam turbine problems | 279 | 277 | 45558.96 | 1660073.9364
4500-Rotor windings (including damper windings and fan blades on hydro units) | 32 | 32 | 3746.41 | 2232015.6308
4510-Rotor collector rings | 6 | 6 | 734.09 | 544804.8689
4511-Rotor; General | 58 | 58 | 9421.18 | 3192921.9373
4520-Stator windings; bushings; and terminals | 46 | 46 | 4871.69 | 4018330.7598
4530-Stator core iron | 4 | 4 | 2415.61 | 2975682.4844
4535-Stator; General | 64 | 64 | 8408.49 | 2126154.1273
4536-Generator heaters | 1 | 1 | 53 | 55173
4540-Brushes and brush rigging | 48 | 47 | 6687.43 | 184015.9476
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 122 | 120 | 8230.5 | 609894.6624
4551-Generator bearings | 81 | 81 | 15733.05 | 2564097.2053
4552-Generator lube oil system | 101 | 101 | 5903.2 | 228017.3975
4555-Bearing cooling system A | 47 | 47 | 2397.96 | 26815.4372
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 168 | 160 | 20468.54 | 3893892.2706
4570-Generator casing | 9 | 9 | 797.3 | 445732.7848
4580-Generator end bells and bolting | 1 | 1 | 175 | 110034.1665
4590-Generator brakes | 46 | 46 | 3540.49 | 274939.8396
4600-Exciter drive - motor | 34 | 34 | 3057.15 | 93918.5855
4601-Exciter field rheostat | 25 | 25 | 2462.81 | 36756.6632
4602-Exciter commutator and brushes | 65 | 65 | 11396.64 | 736797.3277
4603-Solid state exciter element | 57 | 55 | 7391.76 | 1041822.2567
4604-Exciter drive - shaft | 4 | 4 | 132.92 | 182283.6779
4605-Exciter transformer | 39 | 39 | 6489.96 | 350100.5821
4609-Other exciter problems | 586 | 586 | 83031.8 | 4194400.843
4610-Hydrogen cooling system piping and valves | 32 | 32 | 5483.48 | 109489.7588
4611-Hydrogen coolers | 69 | 69 | 10227.58 | 552549.8592
4612-Hydrogen storage system | 6 | 6 | 242.62 | 6219.7902
4613-Hydrogen seals | 17 | 17 | 3486.17 | 646634.5772
4619-Other hydrogen system problems | 32 | 32 | 6905.65 | 451116.4917
4620-Air cooling system | 47 | 47 | 4225.94 | 110927.1018
4630-Liquid cooling system | 61 | 61 | 15194.83 | 279025.2931
4640-Seal oil system and seals A | 29 | 29 | 6511.8 | 287100.9093
4650-Other cooling system problems | 59 | 59 | 17838.06 | 539482.3437
4700-Generator voltage control | 205 | 204 | 39262.85 | 1802424.4945
4710-Generator metering devices | 66 | 66 | 9371.81 | 174165.3939
4720-Generator synchronization equipment | 258 | 257 | 23961.2 | 428514.4106
4730-Generator current and potential transformers | 87 | 87 | 21373.86 | 1051912.3128
4740-Emergency generator trip devices | 204 | 204 | 36400.95 | 2058619.8508
4750-Other generator controls and metering problems | 326 | 322 | 27158.67 | 444927.8062
4800-Generator main leads | 47 | 47 | 5485.38 | 1047502.3309
4805-Generator Bus Duct Cooling System | 21 | 21 | 3096.91 | 25054.114
4810-Generator output breaker | 354 | 350 | 33685.71 | 1355513.4267
4830-Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 8 | 8 | 875.4 | 376302.1297
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 6 | 6 | 671.4 | 21313.7697
4840-Inspection E | 2 | 2 | 176.35 | 704.8815
4841-Generator doble testing | 1 | 1 | 47.2 | 491.6666
4842-Reactive and capability testing | 5 | 5 | 865.25 | 1541.6781
4850-Core monitor alarm | 2 | 2 | 210.94 | 1748.7879
4860-Generator Neutral Grounding Equipment | 28 | 28 | 5841.81 | 820233.954
4899-Other miscellaneous generator problems | 447 | 444 | 48907.19 | 4218210.459
5000-Inlet air ducts A | 15 | 15 | 2184.59 | 127063.3086
5001-Inlet air vanes / nozzles | 145 | 145 | 17636.27 | 282784.3044
5002-Inlet air filters A | 148 | 148 | 9321.99 | 144425.3759
5004-Inlet air chillers B | 62 | 62 | 669.08 | 71188.0378
5005-Inlet air evaporative coolers B | 43 | 43 | 585.31 | 43013.7748
5006-Inlet air foggers B | 8 | 8 | 410.61 | 5871.436
5009-Other inlet air problems A | 99 | 99 | 6344.56 | 185753.1583
5010-High pressure shaft D | 5 | 5 | 788 | 262705.1832
5011-High pressure bearings C | 1 | 1 | 51 | 20721.3
5012-High pressure blades/buckets B | 108 | 103 | 13291.3 | 2849414.6772
5013-Compressor casing and bolts | 2 | 2 | 332.16 | 2796.6986
5014-Compressor diaphragms | 4 | 4 | 630 | 24236.8332
5015-Compressor seals | 4 | 4 | 416 | 3126.2
5016-High pressure compressor bleed valves | 138 | 137 | 19122.26 | 209577.6124
5017-Low pressure compressor bleed valves | 63 | 61 | 6252.39 | 36375.0199
5019-Other high pressure problems A | 13 | 13 | 1320.67 | 230809.5753
5021-Low pressure bearings D | 3 | 3 | 345 | 3063.7666
5022-Low pressure blades/buckets A | 17 | 17 | 1254.1 | 689500.3163
5029-Other low pressure problems E | 9 | 9 | 1163 | 42570.6828
5035-Compressor Washing | 11 | 11 | 584.4 | 5075.3858
5037-Inlet bleed heat valve | 27 | 27 | 3186.66 | 17265.219
5039-Other compressor problems | 103 | 102 | 9096.92 | 590710.4884
5040-Fuel tanks B | 10 | 10 | 373.4 | 161.0016
5041-Fuel piping and valves A | 587 | 582 | 78166.11 | 645113.3412
5042-Fuel nozzles/vanes B | 68 | 67 | 9411.14 | 222015.403
5043-Fuel filters A | 28 | 28 | 4527.6 | 39128.575
5044-Liquid fuel oil pump A | 46 | 44 | 2631.5 | 243567.2175
5046-Liquid fuel oil transfer/forwarding pump B | 15 | 15 | 1586.52 | 5942.3388
5047-Liquid fuel purge system A | 27 | 27 | 3572.68 | 42670.4694
5048-Gas fuel system B | 619 | 594 | 66891.89 | 737522.9846
5049-Other fuel system problems B | 393 | 377 | 58532.38 | 934873.3083
5050-Ignition system A | 333 | 322 | 39183.86 | 215759.5296
5051-Pilot fuel piping and valves A | 89 | 88 | 10291.75 | 42909.6845
5052-Pilot fuel nozzles/vanes B | 11 | 11 | 1786.3 | 11619.1697
5054-Water Injection System (Gas Turbine) | 173 | 173 | 15504.11 | 136963.7589
5060-Atomizing air system B | 36 | 36 | 5400.8 | 82927.1435
5065-NOx water injection system including pumps | 79 | 79 | 5208.59 | 30137.1442
5066-NOx Steam Injection System | 18 | 18 | 2383.56 | 17937.0578
5070-Combustor casing A | 14 | 14 | 2168.49 | 70912.133
5071-Combustor liner B | 7 | 7 | 1738 | 75751.2829
5072-Combustor caps B | 6 | 6 | 1040 | 83156.6831
5073-Flame scanners B | 95 | 94 | 10295.07 | 54285.5775
5074-Flashback including instruments | 58 | 58 | 6230.75 | 1253944.876
5075-Blade Path Temperature Spread A | 185 | 185 | 28932.41 | 212547.857
5079-Other combustor problems B | 313 | 307 | 40835.16 | 575353.4419
5080-High pressure shaft C | 7 | 7 | 717.6 | 755722.8333
5081-High pressure bearings D | 15 | 15 | 1353.4 | 178376.2728
5082-High pressure blades/buckets A | 18 | 18 | 1768.7 | 592762.1813
5084-High pressure casing/expansion joints | 5 | 5 | 429 | 19290.2666
5085-Interstage gas passages - HP | 11 | 11 | 661.98 | 113976.8899
5086-High pressure shaft seals A | 1 | 1 | 54 | 912.6
5087-Thrust Bearing | 3 | 3 | 259.78 | 57.8722
5088-Gas turbine cooling steam | 15 | 15 | 1855.3 | 7147.514
5089-Other high pressure problems B | 20 | 20 | 2611.45 | 294035.331
5090-Low pressure shaft A | 1 | 1 | 48 | 8
5091-Low pressure bearings A | 4 | 4 | 537.9 | 92220.7207
5092-Low pressure blades/buckets D | 22 | 21 | 1937.2 | 555567.0229
5094-Low pressure casing/expansion joints A | 4 | 4 | 610.6 | 17121.0031
5096-Low pressure shaft seals | 5 | 5 | 310 | 52245.3332
5097-Other low pressure problems B | 15 | 15 | 928.62 | 120742.1663
5098-Expansion joints A | 5 | 5 | 665 | 12196.133
5099-HP to LP coupling | 2 | 2 | 57.5 | 481.0833
5100-Chamber A | 7 | 7 | 719 | 11593.8331
5102-Vanes/nozzles A | 3 | 3 | 129 | 28830.05
5103-Silencer B | 2 | 2 | 97.02 | 360.591
5105-Diverter Dampers B | 21 | 21 | 2081.88 | 40633.6292
5106-Exhaust Stack | 19 | 19 | 1015.35 | 285895.0489
5108-High engine exhaust temperature A | 158 | 157 | 17686.59 | 532995.7563
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 157 | 156 | 19634.97 | 513121.6188
5110-Lube oil system - general | 229 | 228 | 16826.2 | 734113.337
5111-Lube oil pumps B | 74 | 74 | 9801.85 | 148267.8784
5112-Lube oil coolers B | 26 | 26 | 2623.99 | 30472.5447
5113-Lube oil valves/piping | 25 | 25 | 2616.57 | 171384.2266
5114-Lube oil filters | 14 | 14 | 740.59 | 20709.5715
5115-Oil vapor extractor | 25 | 25 | 1884.7 | 24658.4194
5116-Power Augmentation System Equipment B | 23 | 23 | 691.23 | 10621.2176
5117-Power augmentation piping | 2 | 2 | 420 | 5591.6165
5118-Power augmentation valves | 2 | 2 | 26 | 3157.8667
5119-Power augmentation controls | 3 | 3 | 496.6 | 323.8465
5120-Hydraulic oil system A | 161 | 159 | 19857.26 | 354559.2745
5121-Hydraulic oil system pumps | 12 | 12 | 990.23 | 19459.2297
5122-Hydraulic oil system piping/valves | 43 | 43 | 6135.31 | 67827.82
5130-Starting system (including motor) A | 461 | 461 | 55306.85 | 1354505.9778
5140-Battery and charger system B | 22 | 22 | 1564.2 | 11889.4731
5150-Turning gear and motor C | 59 | 59 | 5374.36 | 431980.5867
5151-Load gear compartment B | 6 | 6 | 465.24 | 3901.1138
5160-Cooling and seal air system B | 139 | 139 | 20208.23 | 228354.4012
5170-Cooling water system A | 33 | 33 | 3883.11 | 38887.813
5180-Anti-icing system A | 13 | 13 | 1001.25 | 47204.5163
5190-Other auxiliary system problems A | 143 | 143 | 15860.87 | 240348.2887
5200-Reduction gear B | 6 | 6 | 519.31 | 22474.0267
5201-Load shaft and bearings A | 19 | 19 | 1972.5 | 48373.699
5205-Main coupling between the turbine and generator A | 1 | 1 | 36 | 777.6
5206-Gas Turbine Clutch | 16 | 16 | 1294.4 | 45449.7163
5210-Intercoolers A | 7 | 7 | 1037.07 | 28796.7818
5220-Regenerators A | 1 | 1 | 46 | 80.5
5230-Heat shields C | 9 | 9 | 696.26 | 54015.2302
5240-Fire detection and extinguishing system B | 176 | 176 | 24843.9 | 336207.1537
5241-Fire in unit A | 16 | 16 | 2143.2 | 203943.8592
5245-Gas Turbine Control System - data highway | 46 | 46 | 4806.17 | 70530.0511
5246-Gas Turbine Control System - hardware problems (including card failure) | 322 | 321 | 39459.76 | 457897.3658
5247-Gas Turbine Control System - internal and termination wiring | 31 | 31 | 3085.4 | 36159.8134
5248-Gas Turbine Control System - logic problems | 103 | 102 | 13859.6 | 62293.704
5249-Gas Turbine Control System - upgrades | 27 | 27 | 3720.19 | 127543.4444
5250-Other Controls and instrumentation Problems A | 629 | 625 | 66817.09 | 502032.8185
5255-Computer | 35 | 35 | 3746.1 | 44586.6946
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 7 | 7 | 519 | 196012.8332
5261-Gas turbine/compressor washing | 19 | 19 | 1702.64 | 14167.3537
5262-Gas turbine exchange | 4 | 4 | 116.1 | 51448.1216
5269-Combustion inspection (CI) | 2 | 2 | 361.3 | 17339.1449
5270-Hot end inspection B | 3 | 3 | 237 | 17157.3
5272-Boroscope inspection A | 18 | 18 | 1924.79 | 556630.842
5274-General unit inspection A | 8 | 8 | 974 | 394106.6831
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 28 | 28 | 3054.3 | 368117.2008
5285-Gas turbine vibration | 236 | 233 | 21048.66 | 2992988.1408
5286-Gas Turbine lockout cause by OEM specifications | 23 | 23 | 3412 | 33997.7041
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 78 | 39 | 2818.48 | 11609.2216
5298-Main gas filter | 2 | 2 | 356.2 | 432.3532
5299-Other miscellaneous gas turbine problems | 409 | 407 | 42572.75 | 1975416.2051
5400-Inlet air ducts B | 3 | 3 | 137.2 | 280.6333
5401-Inlet air vanes/noozles | 16 | 16 | 1103.8 | 8215.4832
5402-Inlet air filters B | 4 | 4 | 123.91 | 286.0384
5403-Inlet and exhaust cones | 1 | 1 | 42.9 | 183.755
5404-Inlet air chillers A | 12 | 12 | 87.74 | 2276.2171
5405-Inlet air evaporative coolers A | 4 | 4 | 101 | 3743.0833
5406-Inlet air foggers A | 11 | 11 | 216.7 | 175.8949
5409-Other inlet air problems B | 13 | 13 | 345.5 | 1953.0966
5410-High pressure shaft B | 2 | 2 | 90 | 42.75
5412-High pressure blades/buckets C | 11 | 11 | 187.8 | 15178.2583
5413-Other high pressure problems D | 7 | 7 | 311.79 | 32010.6931
5414-Compressor diaphragms/vanes | 4 | 4 | 366.4 | 1192.5583
5420-Low pressure shaft C | 1 | 1 | 47 | 25.0667
5422-Low pressure blades/buckets C | 3 | 3 | 131 | 26702.2999
5429-Other low pressure problems D | 4 | 4 | 142 | 121.3666
5435-Jet Engine Compressor Washing | 2 | 2 | 193 | 1201.4833
5439-Jet engine other compressor problems | 21 | 21 | 1071.51 | 33264.4082
5440-Fuel tanks A | 5 | 5 | 129 | 7651.6167
5441-Fuel piping and valves B | 105 | 103 | 4444.69 | 45592.1076
5442-Fuel nozzles/vanes A | 8 | 8 | 332.3 | 11035.9266
5443-Fuel filters B | 9 | 9 | 463.8 | 7406.9432
5444-Liquid fuel oil pump B | 18 | 18 | 472.2 | 5978.1198
5445-Liquid fuel oil transfer/forwarding pump A | 8 | 8 | 256 | 3798.95
5446-Liquid fuel purge system B | 6 | 6 | 421.45 | 1250.7998
5447-Gas fuel system A | 117 | 116 | 5547.49 | 149243.6523
5449-Other fuel system problems A | 118 | 112 | 4377.48 | 53184.0219
5450-Ignition system B | 44 | 43 | 1817.19 | 10607.474
5451-Pilot fuel piping and valves B | 1 | 1 | 163 | 10.8666
5454-Water injection system (Jet Engine) | 73 | 73 | 2715.61 | 12922.7554
5455-Fuel nozzle/vane cooling air system | 2 | 2 | 81 | 702.9333
5460-Atomizing air system A | 11 | 11 | 807.7 | 50713.8397
5471-Combustor liner A | 1 | 1 | 45 | 191211
5473-Flame scanners A | 26 | 26 | 1770.74 | 29377.649
5475-Blade Path Temperature Spread B | 57 | 54 | 7488.9 | 176702.192
5479-Other combustor problems A | 41 | 41 | 2234.9 | 48117.2877
5480-High pressure shaft A | 2 | 2 | 87.5 | 89.0416
5481-High pressure bearings A | 1 | 1 | 40 | 26
5482-High pressure blades/buckets D | 109 | 100 | 852.78 | 353248.0714
5486-High pressure shaft seals B | 2 | 2 | 56 | 6268.7333
5487-Thrust Bearing/jet | 2 | 2 | 40.7 | 831.1883
5489-Other high pressure problems C | 13 | 13 | 518.55 | 272338.9632
5490-Low pressure shaft B | 3 | 3 | 139.5 | 2584.125
5491-Low pressure bearings C | 2 | 2 | 40.1 | 108.35
5492-Low pressure blades/buckets B | 5 | 5 | 197 | 58419.2999
5497-Other low pressure problems C | 6 | 6 | 266 | 184177.5999
5501-Hoods A | 1 | 1 | 33 | 112.2
5503-Silencer A | 2 | 2 | 90 | 7677
5504-Cones B | 2 | 2 | 269.6 | 30577.1332
5505-Diverter Dampers A | 1 | 1 | 119 | 103.1333
5508-High engine exhaust temperature B | 28 | 27 | 807.68 | 5214.9937
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 19 | 19 | 822.08 | 34454.6266
5510-Lube oil system A | 189 | 188 | 7926.26 | 156683.2185
5516-Power Augmentation System Equipment A | 18 | 17 | 511.1 | 3074.3498
5520-Hydraulic oil system B | 29 | 29 | 1598.4 | 14936.4128
5530-Starting system (including motor) B | 81 | 81 | 4138.7 | 75066.6904
5540-Battery and charger system A | 3 | 3 | 306.5 | 2632.2331
5550-Turning gear and motor B | 2 | 2 | 155 | 91.1666
5560-Cooling and seal air system A | 25 | 25 | 1096.9 | 5182.1113
5570-Cooling water system B | 52 | 52 | 645.76 | 11255.7967
5580-Anti-icing system B | 17 | 17 | 691.2 | 3061.394
5590-Other auxiliary system problems B | 94 | 94 | 3772.28 | 80235.8932
5601-Load shaft and bearings B | 6 | 6 | 612 | 11359.3997
5605-Main coupling between the turbine and generator B | 5 | 5 | 198.1 | 15565.3199
5606-Jet Engine Clutch | 5 | 5 | 203.4 | 29868.1449
5610-Intercoolers B | 4 | 4 | 131.1 | 707.3333
5620-Regenerators B | 1 | 1 | 20 | 175200
5630-Heat shields A | 3 | 3 | 45 | 2966.25
5640-Fire detection and extinguishing system A | 49 | 49 | 2048.2 | 17525.6095
5641-Fire in unit B | 1 | 1 | 50 | 2418.3333
5645-Jet Engine Control System - data highway | 38 | 38 | 1609.43 | 9872.2879
5646-Jet Engine Control System - hardware problems (including card failure) | 80 | 80 | 3295.24 | 28505.7923
5647-Jet Engine Control System - internal and termination wiring | 13 | 13 | 559.1 | 10252.0515
5648-Jet Engine Control System - logic problems | 45 | 45 | 2018.3 | 17244.0592
5649-Jet Engine Control System - upgrades | 3 | 3 | 202 | 1042.6833
5650-Other Controls and instrumentation Problems B | 148 | 148 | 7303.29 | 53447.2495
5660-Major overhaul (use for non-specific overhaul only; see page B-1) C | 6 | 6 | 270 | 12390.9999
5661-Engine/compressor washing | 4 | 4 | 113 | 90.4499
5662-Engine exchange | 8 | 8 | 226.9 | 16717.7582
5665-Engine shafts and bearings | 3 | 3 | 92 | 231186.9916
5670-Hot end inspection A | 1 | 1 | 21 | 6937.35
5672-Boroscope inspection B | 1 | 1 | 47.2 | 154.9733
5674-General unit inspection B | 10 | 10 | 433.49 | 11416.9753
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 49 | 49 | 2411.64 | 6361.6541
5685-Engine vibration | 119 | 119 | 4196.36 | 387662.5078
5686-Jet Engine lockout cause by OEM specifications | 10 | 10 | 396 | 15551.8499
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 3 | 3 | 34 | 165.7667
5695-Synchronous condenser equipment B | 9 | 9 | 271 | 26294.7499
5699-Other miscellaneous jet engine problems | 103 | 97 | 3388.9 | 259780.2818
5710-Cylinders | 7 | 6 | 62 | 355.3833
5711-Cylinder heads | 17 | 16 | 165 | 41.3833
5740-Turbo charger | 1 | 1 | 9 | 9.3
5790-Vibration | 1 | 1 | 1 | 404
5799-Other engine problems | 13 | 12 | 24.96 | 2167.0683
5800-Lube oil system C | 6 | 6 | 16.43 | 6438.4407
5805-Cooling system | 11 | 11 | 88.69 | 613.7385
5815-Fuel system | 26 | 24 | 179.58 | 285.0216
5820-Start system | 23 | 20 | 170.2 | 427.0033
5849-Other engine auxiliaries problems | 3 | 3 | 15.24 | 51.5713
5850-Governor | 6 | 6 | 20.56 | 14132.8155
5855-Engine control system | 12 | 12 | 258.13 | 1877.323
5870-Other engine control problems | 3 | 3 | 25.24 | 36.044
5880-Internal Combustion/Reciprocating Engines unit overhaul | 1 | 1 | 9 | 1296
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 54 | 54 | 1013.33 | 82445.2287
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 44 | 44 | 6495.26 | 130871.4401
6005-HP Evaporator tubes | 17 | 17 | 1737.15 | 127769.8445
6006-IP Evaporator tubes | 2 | 2 | 737.7 | 41934.1048
6007-LP Evaporator tubes | 8 | 8 | 1328.14 | 87715.3245
6010-HP superheater | 37 | 37 | 5785.54 | 440138.4129
6011-HP reheater | 13 | 13 | 1823.4 | 112613.9462
6012-HP economizer | 27 | 27 | 3135.9 | 265340.0659
6020-IP superheater | 5 | 5 | 910 | 44600.0166
6021-IP reheater | 12 | 12 | 1634.05 | 114723.606
6022-IP economizer | 6 | 6 | 885 | 33806.2498
6032-LP economizer | 14 | 14 | 2325.3 | 93673.3429
6090-Other HRSG tube Problems | 16 | 16 | 1649.24 | 91528.8628
6100-Steam turbine to gas turbine coupling. For additional codes; use Fossil Steam Cause Codes 4000 to 4499. | 14 | 14 | 1492.5 | 8427.5494
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 16 | 16 | 2482.67 | 72190.0338
6111-HP steam relief/safety valves | 6 | 6 | 843.5 | 10923.0332
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 26 | 26 | 4986.92 | 50764.4558
6113-Other HP steam system problems | 15 | 15 | 2353.7 | 43067.9042
6114-HP steam isolation/boundary valves | 5 | 5 | 746 | 28421.4163
6120-IP steam piping up to turbine stop valves - Between 200 & 600 PSIG (see 0790 for piping supports) | 6 | 6 | 1035.8 | 65186.9032
6121-IP steam relief/safety valves | 9 | 9 | 1328.04 | 33772.5266
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 6 | 6 | 1077 | 3546.4331
6123-Other IP steam system problems | 1 | 1 | 15 | 77.75
6124-IP steam isolation/boundary valves | 2 | 2 | 1186 | 17054.9664
6130-LP steam piping up to turbine stop valves - Less than 200 PSIG (see 0790 for piping supports) | 1 | 1 | 24 | 2964
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 11 | 11 | 1944.51 | 16464.9435
6133-Other LP steam system problems | 14 | 14 | 2138 | 34403.2497
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 57 | 57 | 9984.81 | 179731.2368
6135-LP steam isolation/boundary valves | 4 | 4 | 766 | 12271.2332
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 16 | 16 | 3043.9 | 21087.2054
6141-HP Desuperheater/attemperator valves | 40 | 40 | 5980.1 | 112517.8855
6142-HP Desuperheater/attemperator spray nozzles | 3 | 3 | 424.3 | 8203.9149
6144-Other HP desuperheater/attemperator problems | 9 | 9 | 1352.4 | 4377.9362
6145-IP Desuperheater/attemperator piping - Between 200-600 PSIG | 3 | 3 | 442 | 2248.8166
6146-IP Desuperheater/attemperator valves | 4 | 4 | 600 | 3653.9164
6151-LP Desuperheater/attemperator valves | 2 | 2 | 304 | 6199.5999
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 4 | 4 | 820 | 3174.8331
6161-HP Startup bypass system valves | 34 | 34 | 6630.14 | 112088.2353
6163-Other HP startup bypass system problems | 2 | 2 | 736.7 | 1222.5564
6164-HP Startup bypass instrumentation and controls | 35 | 35 | 5727.16 | 19614.0223
6170-IP Startup bypass system piping (including drain lines up to heaters or condenser) - Between 200-600 PSIG | 1 | 1 | 65 | 1022.6666
6171-IP Startup bypass system valves | 31 | 31 | 5895.99 | 155846.4096
6173-Other IP startup bypass system problems | 2 | 2 | 438.7 | 1586.9664
6174-IP Startup bypass instrumentation and controls | 12 | 12 | 1969.2 | 34282.1729
6180-LP Startup bypass system piping (including drain lines up to heaters or condenser) - Less than 200 PSIG | 1 | 1 | 234 | 698.0999
6181-LP Startup bypass system valves | 1 | 1 | 231 | 223.2998
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 91 | 91 | 15801.44 | 61632.0256
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 123 | 123 | 15520.3 | 722161.1131
6399-Other coal gasification equipment problems | 2 | 2 | 520 | 875.3332
6410-Steam wells/steam field piping problems | 46 | 41 | 264 | 7222.9166
6430-Unit H2S emission limitations ? regulatory | 1 | 1 | 29 | 32.8667
6440-H2S abatement system problems ? general | 2 | 2 | 17 | 41.9333
6499-Geothermal | 15 | 15 | 336 | 271.1499
7000-Shaft B | 2 | 2 | 47 | 111164.4167
7001-Shaft packing | 33 | 33 | 2578.18 | 293750.8217
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 41 | 41 | 3458.75 | 188453.9687
7007-Bearings A | 53 | 52 | 5000.12 | 836194.9135
7008-Bearing cooling system B | 41 | 41 | 2260.08 | 46881.9537
7009-Bearing Oil System | 82 | 82 | 5204.47 | 150895.9238
7010-Runner cavitation damage | 4 | 4 | 338.02 | 106226.1333
7011-Other runner problems | 26 | 26 | 739.22 | 786879.3474
7020-Nozzle assembly | 6 | 6 | 270.95 | 2769.3941
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 23 | 23 | 1467.02 | 452585.8997
7050-Turbine governor | 246 | 240 | 22539.97 | 847617.2458
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 59 | 59 | 4475.1 | 481781.6644
7053-Governor Oil System | 82 | 82 | 5660.17 | 74256.4648
7099-Other turbine problems | 227 | 221 | 8563.23 | 623395.1127
7100-Upper reservoir dams and dikes | 9 | 9 | 276.4 | 71599.5666
7101-Lower reservoir dams and dikes | 20 | 20 | 558 | 47242.1582
7102-Auxiliary reservoir dams and dikes | 2 | 2 | 103 | 71861.8666
7110-Intake channel or flume (including trash racks) | 105 | 105 | 4516.84 | 138511.0503
7111-Intake tunnel | 21 | 21 | 2420.79 | 26751.7954
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 64 | 61 | 2161.9 | 66659.6771
7120-Headgates | 46 | 45 | 3690.89 | 174241.3875
7121-Shutoff valves | 41 | 40 | 4863.82 | 246924.3382
7123-Shutoff valve bypass line and valve | 9 | 9 | 2356 | 65051.7992
7124-Penstock | 18 | 18 | 943.87 | 64741.4077
7130-Spiral case | 7 | 7 | 1051.53 | 208752.5709
7140-Wicket gate assembly | 20 | 19 | 2257.28 | 220749.1399
7141-Wicket gate operating mechanism or positioner | 26 | 26 | 1876.07 | 52911.4528
7142-Wicket gate shear pin | 165 | 165 | 10554.89 | 215341.8706
7160-Pressure regulating valve | 5 | 5 | 369.62 | 1186.4165
7162-Relief valve and vacuum breakers | 6 | 6 | 527 | 23747.5499
7170-Draft tube | 11 | 11 | 1891.4 | 102674.0112
7180-Tailrace | 54 | 54 | 2502.86 | 123696.6454
7181-Tail water depressing equipment | 9 | 9 | 600.34 | 3095.8869
7190-Dewatering and rewatering equipment | 3 | 3 | 152.11 | 3544.9365
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 149 | 149 | 1162.68 | 115306.5179
7200-Major overhaul (use for non-specific overhaul only; see page B-1) B | 2 | 2 | 83.3 | 19653.9333
7201-Inspection A | 7 | 7 | 357.45 | 85170.2041
7210-Canals (including siphons; radial gates; and spills) | 3 | 3 | 85.1 | 2007.1391
7220-Unit out of service due to common penstock with unit under repair | 8 | 8 | 394.27 | 4200.4836
7230-Pony motor (pumped storage units only) | 4 | 4 | 1304 | 22345.5332
7240-Powerhouse Substructure | 3 | 3 | 264 | 4055.6083
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 25 | 25 | 1597.71 | 155035.271
7820-Bearings B | 12 | 12 | 881.1 | 287338.0482
7830-Blades | 4 | 4 | 39 | 86112
7850-Spacers | 1 | 1 | 56.5 | 273.0833
7910-Outer exhaust casing | 1 | 1 | 29 | 104.8833
7920-Lube oil system B | 22 | 22 | 807.15 | 81891.8645
7930-Controls and instrumentation A | 29 | 29 | 2000.56 | 23331.7546
7960-Other expander turbine problems | 10 | 10 | 630.84 | 90305.1715
8000-Chemical feed storage; mill feeders; and conveyors | 6 | 6 | 720.7 | 4029.9133
8006-Weigh feeders | 2 | 2 | 320 | 973.3333
8010-Crushers/mills | 27 | 27 | 3824.77 | 46943.732
8020-Mill slurry tanks supply problems | 28 | 27 | 2139.16 | 20327.2464
8040-Slurry transfer pumps and motors | 16 | 16 | 3211 | 21068.9325
8050-Chemical unavailability | 3 | 3 | 900 | 1614.9999
8099-Other chemical supply problems | 8 | 8 | 1221.66 | 11889.8917
8100-Scrubber/absorber tower or module | 185 | 183 | 20908.91 | 376877.2365
8110-Spray nozzles | 2 | 2 | 126 | 2784.2499
8120-Spray pumps and motors | 17 | 17 | 3891 | 83655.6654
8125-Scrubber recycle (liquid) pumps | 53 | 53 | 5264 | 57197.4483
8127-Scrubber recycle (liquid) pump motors | 8 | 8 | 546 | 5674.7666
8130-Recirculation tanks including agitators | 13 | 13 | 1677 | 11391.8993
8140-Reaction tanks including agitators | 9 | 9 | 2821 | 95196.999
8150-Tubes | 25 | 24 | 4169 | 84007.999
8160-Mist eliminators/demisters and washdown | 55 | 55 | 3815 | 294131.1988
8199-Other scrubber problems | 68 | 67 | 7236.01 | 169720.5094
8200-Piping | 27 | 27 | 4171.43 | 32490.7067
8210-Valves | 12 | 12 | 4013.32 | 105678.1138
8220-Strainers or filters | 5 | 5 | 1811 | 67348.0993
8230-Ducting | 6 | 6 | 1602 | 46442.3327
8235-Demister | 5 | 5 | 135 | 59.3999
8240-Bypass dampers | 1 | 1 | 554 | 10008.933
8250-Dampers other than bypass | 15 | 15 | 2397.61 | 43667.074
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 124 | 124 | 17014.25 | 535279.6238
8261-Scrubber booster I.D. fan drive | 40 | 40 | 5649.85 | 90037.3677
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 44 | 44 | 6459.75 | 230488.5434
8264-Scrubber booster I.D. fan blades (fan specific to the scrubber) | 6 | 6 | 390 | 16060.2999
8265-Scrubber ID fan dampers | 3 | 3 | 183 | 7567.2166
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 12 | 12 | 1806.07 | 4476.4444
8271-Scrubber booster F.D. fan drive | 23 | 23 | 2316.31 | 117090.8907
8272-Scrubber booster F.D. fan vibration (fan specific to the scrubber) | 3 | 3 | 401.83 | 13969.6738
8274-Scrubber booster F.D. fan blades (fan specific to the scrubber) | 1 | 1 | 122 | 150.4666
8275-Scrubber FD fan dampers | 2 | 2 | 550 | 2096.6666
8280-Reagent feed piping | 11 | 11 | 1887.2 | 11153.9293
8290-Demister wash piping assembly | 2 | 2 | 325.5 | 3275.8749
8299-Other piping; ducting; damper; and fan problems | 11 | 11 | 1762.9 | 54450.8377
8310-Waste disposal/recovery pumps | 1 | 1 | 320 | 11285.3331
8320-Waste disposal ponds | 1 | 1 | 77 | 57.75
8325-Ash disposal problems | 23 | 23 | 858.71 | 47018.795
8330-Dewatering equipment (thickener; centrifuge; etc.) | 18 | 16 | 8132 | 71077.6662
8340-Centrifuge/vacuum filter | 5 | 5 | 1845 | 12097.5
8349-Other waste disposal and recovery problems | 4 | 4 | 1620 | 32534.9995
8399-Solids conveying and mixing system problems | 1 | 1 | 720 | 10859.9998
8410-Scrubber instruments and controls | 11 | 11 | 1586.01 | 19397.2103
8415-Liquid level controls | 15 | 15 | 3305.8 | 27536.3753
8425-Miscellaneous mechanical failures | 4 | 4 | 423 | 1923.0665
8426-Miscellaneous electrical failures | 9 | 9 | 1834.29 | 6434.3059
8430-Stack damage related to scrubber system | 1 | 1 | 190 | 10323.3333
8460-Testing | 4 | 4 | 315 | 820.1999
8499-Other miscellaneous wet scrubber problems | 76 | 76 | 4099.77 | 77175.1332
8500-Slurry storage and feed tanks | 5 | 5 | 606.3 | 2412.9666
8501-Reagent storage; feed bins; and conveyors | 10 | 10 | 1270 | 4876.2329
8504-Mills/slakers | 6 | 6 | 1866.56 | 9000.2598
8506-Slurry pipelines | 17 | 17 | 2906.97 | 25502.073
8507-Reagent uploading and transfer systems | 1 | 1 | 264 | 343.2
8508-Reagent unavailability | 2 | 2 | 130 | 443.0833
8510-Slurry mixers and agitators | 4 | 4 | 517 | 11823.4331
8520-Slurry transfer pumps and motors | 5 | 5 | 503.75 | 626.5832
8521-Reagent/slurry problems | 18 | 18 | 1161.6 | 6099.8633
8522-Piping | 1 | 1 | 10 | 42
8523-Valves | 5 | 5 | 576.58 | 2923.0742
8524-Strainers or filters | 6 | 6 | 815.2 | 2203.6964
8525-Ducting | 2 | 2 | 300 | 46700.9999
8528-Dry scrubber instruments and controls | 5 | 5 | 966.2 | 11123.4766
8529-Gas dispersers | 1 | 1 | 40 | 96.6666
8530-Spray towers | 2 | 2 | 380 | 7599.6667
8531-Spray machine/atomizer | 80 | 80 | 5039.66 | 76275.9347
8532-Spray machine/atomizer motors | 7 | 6 | 405 | 22595.5666
8533-Spray machine/atomizer lubrication systems | 9 | 9 | 904 | 3872.4333
8534-Spray machine/atomizer vibration problems | 19 | 19 | 1056.33 | 20331.4711
8535-Fly ash conveyors | 4 | 4 | 760 | 10185.5
8538-Recycle storage and feed tanks including agitators | 1 | 1 | 87 | 3098.6499
8541-Recycle feed bins | 3 | 3 | 856 | 12167.8832
8544-Mechanical failures | 5 | 5 | 385.74 | 4522.5476
8545-Electrical failures | 6 | 6 | 1576 | 13551.433
8546-Major overhaul | 1 | 1 | 211 | 9797.4333
8549-Other dry scrubber problems | 33 | 33 | 2812.64 | 115600.0139
8550-Electrostatic precipitator fouling | 252 | 252 | 22095.04 | 1001923.6542
8551-Electrostatic precipitator field out of service | 860 | 850 | 58723.89 | 958797.4809
8560-Electrostatic precipitator problems | 253 | 253 | 24225.95 | 590664.7206
8580-Mechanical precipitator problems | 15 | 15 | 1553.93 | 25243.2118
8590-Other precipitator problems | 33 | 33 | 3905.96 | 133758.5816
8600-Flue gas additives (furnace injection) | 22 | 22 | 2693.9 | 57485.5592
8601-SO3 mitigation | 9 | 9 | 1643.3 | 22991.9097
8650-Baghouse systems; general | 326 | 316 | 16248.93 | 366062.6916
8651-Bag failures and rebagging | 242 | 242 | 10960.14 | 274278.2641
8653-Inflation and deflation fans and motors | 1 | 1 | 20 | 30
8654-Baghouse booster fans and motors | 28 | 28 | 1973.53 | 46607.312
8655-Structural duct work and dampers | 6 | 6 | 655 | 8254.5998
8656-Controls and instrumentation B | 69 | 69 | 8328.28 | 81551.5185
8657-Ash handling system and hoppers | 82 | 82 | 13809.86 | 498992.4467
8658-Slurry system from precipitators | 2 | 2 | 200 | 795
8670-Emission monitors (other than CEMS) A | 11 | 11 | 1360.94 | 21783.1779
8699-Other miscellaneous pollution control equipment problems | 117 | 116 | 11775.85 | 260223.9109
8700-CEMS Certification and Recertification | 25 | 25 | 2991.72 | 17317.3624
8720-NOx analyzer problems | 60 | 60 | 5566.51 | 83618.9229
8730-CO analyzer problems | 19 | 19 | 1101.41 | 13441.9754
8740-CO2 analyzer problems | 3 | 3 | 307.2 | 1245.7699
8750-O2 analyzer problems | 20 | 20 | 1625.15 | 23702.3238
8760-Opacity monitor problems | 48 | 48 | 3327.18 | 15530.1114
8770-Flow monitor problems | 15 | 15 | 1292.6 | 4825.1031
8780-Data acquisition system problems | 28 | 28 | 2382.56 | 16716.0557
8790-Miscellaneous CEMS problems | 148 | 147 | 10968.52 | 206810.0603
8800-SNCR NOx Reagent | 3 | 3 | 146.73 | 1473.9466
8802-SNCR NOx Control system | 13 | 13 | 1217.1 | 12047.6545
8809-Other SNCR NOx problems | 30 | 30 | 1792.89 | 246964.7129
8810-SCR NOx Reactor | 2 | 2 | 548 | 23817.8666
8811-SCR NOx Reagent | 3 | 3 | 313.23 | 1440.9375
8812-SCR NOxCatalyst | 36 | 36 | 1835.35 | 142079.2235
8813-SCR NOx Injection grid piping/valves | 39 | 39 | 2816.88 | 18376.6032
8816-SCR NOx Plugging | 50 | 50 | 1888.46 | 205141.7515
8817-SCR NOx Control system | 39 | 39 | 4523.48 | 36777.1112
8820-SCR NOx Ammonia injection grid piping/valves | 43 | 43 | 4985.83 | 40086.946
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 22 | 22 | 1994.5 | 16052.6914
8822-SCR NOx Ammonia air blowers | 23 | 23 | 2136.58 | 21829.2107
8823-SCR NOx Other ammonia system problems | 150 | 150 | 12046.71 | 130789.7574
8825-Other SCR NOx problems | 82 | 82 | 7586.49 | 104625.7188
8830-CAH NOx Active catalyst | 1 | 1 | 48.62 | 283.6166
8832-CAH NOx Plugging | 1 | 1 | 78 | 72.8
8840-CO Active catalyst | 3 | 3 | 115 | 498.4
8842-CO Plugging | 2 | 2 | 506.24 | 52691.7625
8845-Other CO reduction problems | 40 | 40 | 1866.35 | 18978.5729
9000-Flood | 137 | 134 | 3448.24 | 395641.0082
9010-Fire; not related to a specific component | 46 | 46 | 2985.21 | 766843.0997
9020-Lightning | 213 | 213 | 26267.76 | 436592.9274
9025-Geomagnetic disturbance | 1 | 1 | 298 | 2682
9030-Earthquake | 3 | 3 | 290 | 2213.6666
9031-Tornado | 9 | 9 | 2395.61 | 60344.1953
9036-Storms (ice; snow; etc) | 99 | 98 | 10963.78 | 331302.3706
9040-Other catastrophe | 42 | 42 | 4444.99 | 2045898.3593
9110-Core coastdown (nuclear) | 25 | 25 | 4158 | 34796.9157
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 762 | 711 | 72860.12 | 2373596.8916
9131-Lack of fuel: Contract or Tariff allows for interruption | 1549 | 1461 | 77759.1 | 3423769.0129
9132-Wet Fuel - Biomass | 72 | 68 | 1238.19 | 15894.4992
9134-Fuel conservation | 277 | 273 | 19659.37 | 924505.9985
9135-Lack of water (hydro) | 2953 | 2765 | 52776.77 | 1786654.2849
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 1 | 1 | 171 | 339.1499
9137-Ground water or other water supply problems | 275 | 274 | 1681.39 | 29628.0778
9160-Other economic problems | 29 | 24 | 2444.19 | 205391.4048
9180-Economic (for internal use at plants only) | 14 | 14 | 844.37 | 141118.3465
9200-High ash content | 349 | 344 | 22788.38 | 103831.6759
9201-High ash content ? (not outside management control) | 28 | 28 | 3645 | 165437.7324
9205-Poor quality natural gas fuel; low heat content | 35 | 35 | 574 | 3987.0665
9210-Low grindability | 11 | 11 | 789.64 | 32425.9599
9211-Low grindability (not outside management control) | 7 | 7 | 253 | 972.2999
9220-High sulfur content | 9 | 9 | 1517.16 | 5583.1593
9221-High sulfur content ? (not outside management control) | 26 | 26 | 2690 | 75891.1159
9240-High sodium content | 1 | 1 | 275 | 10541.6666
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 860 | 846 | 35934.56 | 1340415.2206
9251-Low Btu Coal From Contract For Low Btu Coal | 63 | 62 | 2280.62 | 56978.9431
9270-Wet coal | 1342 | 1333 | 147233.79 | 1689467.7296
9271-Wet coal (not outside management control) | 759 | 757 | 82478.89 | 1443541.8576
9272-Wet Fuel (other than coal) | 1 | 1 | 4.02 | 4.02
9280-Frozen coal | 25 | 25 | 669.1 | 11551.3065
9281-Frozen coal (not outside management control) | 87 | 85 | 9665.8 | 268124.6134
9290-Other fuel quality problems | 668 | 663 | 68780.75 | 1572992.5469
9291-Other fuel quality problems (not outside management control) | 603 | 599 | 24129.56 | 638414.1995
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 2624 | 2576 | 96832.06 | 2780381.9253
9305-Ash disposal problem | 6 | 6 | 554.04 | 22676.0372
9310-Operator training | 7 | 7 | 476.7 | 243746.5295
9320-Other miscellaneous external problems | 1174 | 967 | 42261.66 | 967148.0103
9350-Public Safety/River Rescue | 18 | 18 | 269.25 | 655.1799
9504-Regulatory (environmental) proceedings and hearings - regulatory agency initiated | 1 | 1 | 1.9 | 520.03
9506-Regulatory (environmental) proceedings and hearings - intervenor initiated | 1 | 1 | 24 | 18078.4
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 1 | 1 | 758 | 4358.5
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 189 | 176 | 2366.6 | 270157.6987
9600-SO2 stack emissions (fossil) | 104 | 102 | 6082.67 | 67191.3066
9603-SO2 stack emissions (gas turbine) | 1 | 1 | 188 | 244.4
9604-SO2 stack emissions (jet engines) | 1 | 1 | 5 | 94.5833
9610-NOx stack emissions (fossil) | 223 | 185 | 11277.92 | 286792.0679
9613-NOx stack emissions (gas turbine) | 132 | 129 | 10178.96 | 260561.5997
9614-NOx stack emissions (jet engines) | 62 | 54 | 1403.46 | 6131.9755
9615-NOx stack emissions (Internal Combustion/Reciprocating Engines) | 10 | 9 | 23.11 | 332.5742
9616-CO stack emissions | 151 | 142 | 5617.8 | 92110.6016
9620-Particulate stack emissions (fossil) | 175 | 174 | 13149 | 129214.4628
9630-Opacity (fossil) | 1252 | 1248 | 89995.99 | 1239549.0898
9633-Opacity (gas turbine) | 6 | 6 | 129 | 394.8833
9634-Opacity (jet engines) | 1 | 1 | 43.2 | 28.8
9650-Other stack or exhaust emissions (fossil) | 154 | 154 | 9819.36 | 150921.5069
9653-Other stack or exhaust emissions (gas turbine) | 24 | 22 | 1091.9 | 6193.8963
9654-Other stack or exhaust emissions (jet engines) | 6 | 6 | 180.76 | 1793.7759
9655-Other stack or exhaust emissions (Internal Combustion/Reciprocating Engines) | 2 | 1 | 2.57 | 19.018
9656-Other stack or exhaust emissions testing - fossil | 31 | 31 | 4103.19 | 25504.2883
9657-Other stack or exhaust emissions testing - gas turbine | 5 | 5 | 419 | 21786.2999
9658-Other stack or exhaust emissions testing - jet engines | 1 | 1 | 19.6 | 5.2267
9660-Thermal discharge limits (fossil and nuclear) | 133 | 133 | 7955.43 | 95320.8047
9663-Thermal discharge limits (gas turbine) | 20 | 20 | 277 | 13167.4999
9680-Fish kill (fossil and nuclear) | 2 | 2 | 398 | 1011.5833
9683-Fish kill (gas turbine) | 1 | 1 | 31.5 | 630
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 66 | 66 | 3265.67 | 240516.6961
9693-Other miscellaneous operational environmental limits (gas turbines) | 40 | 40 | 1405.25 | 72145.0745
9694-Other miscellaneous operational environmental limits (jet engines) | 66 | 58 | 1032.1 | 130604.4865
9695-Other miscellaneous operational environmental limits (Internal Combustion/Reciprocating Engines) | 8 | 5 | 12.85 | 885.0652
9696-Other miscellaneous operational environmental limits (hydro and PS) | 34 | 34 | 1180.64 | 36650.5676
9720-Other safety problems | 63 | 63 | 5627.87 | 160812.0412
9900-Operator error | 523 | 523 | 122492.29 | 1593781.8286
9910-Maintenance personnel error | 185 | 185 | 36640.88 | 401060.5936
9920-Contractor error | 71 | 71 | 12468.33 | 378078.1343
9930-Operating procedure error | 50 | 50 | 9001.42 | 458619.1763
9940-Maintenance procdure error | 23 | 23 | 3169.18 | 199412.8406
9950-Contractor procedure error | 8 | 8 | 1755.5 | 422421.849
9960-Staff shortage | 19 | 19 | 1812.8 | 380005.9565
9997-NERC Reliability Standards requirements | 15 | 15 | 831.8 | 301733.8732
9998-Black Start testing | 4 | 4 | 1915 | 6075.8333
9999-Total unit performance testing (use appropriate codes for individual component testing) | 186 | 186 | 6418.77 | 1790341.6129
Total Result | 82676 | 80795 | 8839099.54 | 357982078.6771

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276 | 230 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 693 | 220 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 8.1667 | 10 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3732.4999 | 150 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | U1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437.4166 | 145 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | U3-Forced - Postponed | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.3333 | 70 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 244.9998 | 300 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 498.3333 | 130 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 42.5 | 30 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | U1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1408 | 220 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.9999 | 150 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 45.5 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 120.25 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 161.85 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 41.0667 | 32 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 15.1667 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 53.0833 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 481 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 32.5 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 71.5 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 91 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 126.75 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 67 | 10 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 65 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 554.6667 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 78 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 54.1667 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 104 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 52 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 94.25 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 97.0333 | 41 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 131.2 | 41 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 323.85 | 51 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 91 | 26 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 350.3 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 4601.9 | 51 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 43.9166 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 21.5 | 43 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 310 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 363.4 | 158 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 524.8 | 64 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 798 | 168 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150.825 | 120.66 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.6666 | 80 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 509.2498 | 315 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.7499 | 105 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 982.5 | 131 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.9999 | 120 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 469.3333 | 64 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11 | 11 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.5 | 34 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138 | 12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.3332 | 236 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 357 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 493.95 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 990.8666 | 167 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1144.9999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2038.6999 | 174 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4403.4 | 537 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.1333 | 64 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 325 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 679.25 | 143 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 702.7332 | 254 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1277.8332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.5 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 75.9999 | 228 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 162 | 54 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 172.5666 | 167 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 213.3333 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 251.9999 | 189 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 475.9666 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 575.7 | 303 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 991.683 | 124.74 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1963.3332 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3702.3 | 246 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20461.1665 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 8492.5765 | 205.3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 34.6667 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.5 | 46 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216.8833 | 91 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 434.7 | 189 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1653.8166 | 221 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20119.4998 | 459 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5333 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98.3333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 322.5 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.3333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.5 | 65 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71.8667 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 167.9166 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 406 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 762.8333 | 115 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 844.3666 | 146 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1096.6665 | 350 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1205.3333 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4437 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6709.9165 | 365 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 199.8 | 108 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 207.1999 | 111 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 426.5166 | 163 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1028.2665 | 256 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1072.5 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1122 | 136 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3642.012 | 178.53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101.1 | 6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 167.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 377.6 | 96 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 410.6666 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 673.2 | 36 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 676.4 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2352 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2952 | 246 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1044 | 174 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 462 | 11 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 245.35 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.5 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.1333 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2508.9165 | 253 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 329.0833 | 55 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 359 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1585.95 | 97 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62.3333 | 55 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 100.9833 | 83 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.5 | 2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.7 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.8333 | 22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 264 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 282.3332 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332.9166 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 338.4333 | 142 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 369 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 528 | 240 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 612.5 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 912.5333 | 116 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1118 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2128.4999 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2880 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.6 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.6666 | 185 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79 | 79 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.6666 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 582.5 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 875.6666 | 142 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1738 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4486.6664 | 400 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6730.458 | 352.38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.7999 | 111 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.297 | 59.26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 104.8666 | 121 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 633 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 682.4998 | 234 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1106.2999 | 222 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1240.8 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2305.0833 | 199 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2964.6333 | 151 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3126.9999 | 159 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6339.6664 | 418 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 340.8 | 284 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5311.9997 | 498 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.3332 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 149 | 149 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 225.75 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 239.8 | 22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 326.25 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 443.2999 | 186 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 487.2 | 144 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 585 | 195 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1026.6666 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2606.6666 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5883 | 159 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6781.5 | 274 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.2332 | 254 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210 | 84 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 308 | 308 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 308.75 | 65 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 686.2332 | 173 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 822 | 274 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1328.9 | 274 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3190 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.2667 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.8 | 132 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196.0833 | 181 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 308.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 445.3 | 146 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 592.6666 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 686.6666 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 725.65 | 69 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 751.2666 | 236 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 794.5666 | 121 | 3 | 3 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 813.1666 | 119 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1042.3332 | 236 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1171.6666 | 185 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1530 | 408 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1658.4999 | 186 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3593.8 | 102 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1068.522 | 136.99 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2003.68 | 250.46 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2910 | 291 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20237.9 | 461 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 2578.5 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.6667 | 44 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78 | 2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 97.5 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 121.5 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 203.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 481.6666 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 584.25 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1703 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1987.15 | 33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5261.25 | 305 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7271.9999 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.65 | 43 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.5 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77.2665 | 244 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 176 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 295.8 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 322.5 | 86 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 419.533 | 434 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 640.9482 | 265.22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1211.7331 | 284 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1265 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 3107.1375 | 276.19 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4533.3332 | 400 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3.3333 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 46.3333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.5 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48.25 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 66 | 33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 98.3333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 247.4666 | 128 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 254.8333 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 260.9833 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 437.9 | 87 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 606.0999 | 87 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 620.0333 | 89 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1044.9999 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1111.2666 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2736.25 | 199 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 49.05 | 27 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 53.7 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 56.0473 | 28.99 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 22.9666 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.4 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.25 | 61 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 154.9166 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 414 | 54 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 785.1999 | 156 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 934.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7263.6665 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 396.8 | 62 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6474.9997 | 420 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1278.3333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 519.4916 | 183.35 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2232.2332 | 334 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67656.953 | 541.4 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.8333 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160.0833 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321.5832 | 227 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 430.5 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 436.1499 | 183 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1244.4 | 183 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1318.6666 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1973.3997 | 468 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3502.4332 | 358 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6145.7 | 407 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 389.3951 | 104.77 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5243.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.3 | 6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 144.5833 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 180 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 193.75 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 212.4999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 459 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 560 | 96 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 663.6 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1870.3332 | 310 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 186.2331 | 302 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 80.2666 | 43 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.5 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.4833 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 178.8333 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 492 | 41 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3010 | 301 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1699.5332 | 212 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2066.1 | 291 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.0167 | 23 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.6667 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 206.25 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1161 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1905.4666 | 124 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1995 | 210 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3586.0998 | 282 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129 | 64.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 234.6666 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 244.926 | 136.07 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1046.6664 | 400 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1337.9333 | 244 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36633.3332 | 400 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.25 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.8333 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.75 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 125 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 156.3333 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 318.1999 | 111 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 378 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 606.3332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 660 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 731.4 | 92 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 794.2666 | 92 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2336.3665 | 217 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2886.3999 | 246 | 1 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3869.5 | 355 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 4678.0699 | 207.3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 24.5 | 49 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 29.45 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.2833 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.842 | 48.66 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 167.8333 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1127.4999 | 165 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6830.75 | 445 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4442.1666 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 13160 | 470 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.25 | 11 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132 | 22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 189 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 204 | 102 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 236.25 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 352.3333 | 151 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 552.5 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 706.4166 | 173 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 789.5832 | 379 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 966 | 483 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1249.9999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 653.6666 | 106 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10641.4 | 308 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.2 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.25 | 73 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 116.9666 | 121 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 159 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 364.1666 | 95 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 719.8 | 236 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 866.7166 | 161 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 959.7332 | 236 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2814.1 | 214 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 321.7332 | 152 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 282.2933 | 13.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2136.3332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3987.1665 | 509 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 579.6166 | 83 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 28 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 70 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 28.5 | 9.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 62 | 15.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 21.5 | 21.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 509.3333 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 49 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 34.5 | 11.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 35.625 | 9.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 59.5 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 12.5 | 12.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 831.05 | 33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 42 | 14 | 1 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 63 | 10.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 90 | 22.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 231.1667 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1245.1665 | 241 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 7.7 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 33.7333 | 23 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 26.7 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 57.5167 | 29 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 11 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 27 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2.1667 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 80 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 302.8666 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 911.9666 | 218 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1895.9999 | 288 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 27.6 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 7891.1665 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 322.5333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 482.5 | 193 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2011.9 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 76.0833 | 55 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 88.5 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 477 | 318 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 510.8666 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 590 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 593.5999 | 168 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 804 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 884.5332 | 248 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 920.1998 | 258 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 49.0667 | 32 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 516.6 | 369 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 374.8997 | 489 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2388.3 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 168 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 729.6665 | 398 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 95.2 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 184.8666 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1241.6665 | 298 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1461.2333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1951.1 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 167.1666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 489.0999 | 219 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 163.3666 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 59 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 282.7999 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 470.4 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 549.4 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 102.2666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 6054.55 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1590.9999 | 444 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 196.6666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 536.9 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 777.4666 | 98 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1330.9331 | 368 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 789.6 | 188 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1038.7998 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2695.9332 | 218 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 331.7666 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 310.8 | 168 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1140.8 | 368 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1746.4 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 98.5833 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 601.9999 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1089.5333 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 82.7333 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 204.3999 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 566.2 | 298 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1042.3333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1292.1 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 64 | 48 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 92.4333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 384.0831 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 407.9832 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1863.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 43.0833 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 244.8 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 544.9332 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 638.4 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1459.2666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 291.4166 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 99.45 | 39 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 6240.4166 | 85 | 1 | 1 | 0040-Coal elevators | U1-Forced - Immediate | 650-Fluidized Bed
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 307.1667 | 38 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 431.9333 | 38 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1438.5665 | 419 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1410.6331 | 419 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 694.3872 | 159.02 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4224 | 384 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 937.9999 | 420 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 804.9997 | 420 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.1166 | 33.67 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1205.8666 | 119 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2059.2333 | 163 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8510.76 | 338.4 | 1 | 1 | 0060-Coal crushers including motors | U1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52 | 52 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 166.6666 | 100 | 1 | 1 | 0060-Coal crushers including motors | D3-Forced - Postponed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 132 | 99 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 909 | 202 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 98.5389 | 120.66 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 424.3332 | 268 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 718.6666 | 40 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.5 | 18 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4100.2 | 166 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 942.4665 | 422 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1944.3333 | 190 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 650-Fluidized Bed
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 641.1999 | 168 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 101.5 | 58 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.2167 | 41 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74.5333 | 104 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 214.6666 | 70 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 517.4998 | 270 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 93.22 | 47.4 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.6666 | 40 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 113.75 | 105 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.3333 | 70 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2545.5 | 90 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 5.3833 | 17 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 66 | 11 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1235.3332 | 436 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11671 | 220 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 394.6667 | 32 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1456 | 260 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 370.8333 | 250 | 1 | 1 | 0075-Storage silos/hoppers | D3-Forced - Postponed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2221.3332 | 170 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.65 | 63 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49 | 70 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.9 | 58 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.8 | 9 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 28 | 40 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 69 | 23 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 54.6667 | 20 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7 | 20 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 896.75 | 85 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 43.5 | 30 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35.7 | 51 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120.75 | 63 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 230 | 50 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.1 | 7 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450 | 50 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 861.7997 | 417 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D3-Forced - Postponed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.9167 | 35 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31798.6665 | 280 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 103.4 | 16.5 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 15.8 | 15.8 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 75.65 | 8.5 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 94.575 | 29.1 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 18.2 | 9.1 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 9.3 | 3.1 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102 | 24 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3680.9999 | 270 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 49.95 | 27 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | TRE | Off-Peak | 415.1667 | 47 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 77.9167 | 17 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 1.5833 | 5 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 38.3333 | 20 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 382.5 | 170 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 201.75 | 15 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 12.25 | 5 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 25.65 | 27 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4203.6 | 248 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 19.9 | 6 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 25.8333 | 25 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 7.9167 | 5 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1054 | 120 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1044 | 174 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4488.5 | 470 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10985.2666 | 164 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 4.1333 | 8 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 14.6667 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 3.15 | 27 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | TRE | Winter | 7395 | 17 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.0833 | 65 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 391 | 170 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1051.9999 | 120 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1197.5999 | 144 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 12.3667 | 7 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 19.6667 | 10 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 15.1667 | 26 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 30.25 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 32.9333 | 26 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 807.5 | 50 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 1980 | 45 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 167.9167 | 25 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 812.5 | 25 | 1 | 1 | 0080-Stackers/reclaimers | D3-Forced - Postponed | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 60 | 20 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 150 | 30 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 242.9833 | 61 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1548.75 | 413 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 109.1667 | 50 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.965 | 119.9 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.6666 | 40 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.3015 | 160.67 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 565.3899 | 172.2 | 1 | 1 | 0085-Bunker feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302 | 40 | 1 | 1 | 0085-Bunker feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3933.3332 | 200 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1500 | 60 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155 | 75 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2760 | 40 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 392 | 14 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 713.05 | 54.85 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 972.9 | 414 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.01 | 12.67 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7233.3 | 51.3 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 725 | 100 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.5 | 170 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.75 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 270 | 180 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 428.75 | 343 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2626.5 | 90 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.1958 | 3.25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.1123 | 9.49 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.6666 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132.9999 | 114 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 25 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 42 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4700 | 100 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2701.3999 | 156 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33600 | 100 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 249.0333 | 62 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.2 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 900.9 | 154 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1216.8799 | 172.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.7333 | 64 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.576 | 6.88 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 840.5833 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.9233 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.4517 | 16.7 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183.7666 | 74 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 757.7666 | 254 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5372.2666 | 224 | 1 | 5 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 300 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 64 | 4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1680 | 70 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.08 | 12.54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 508.3333 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1293.4166 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5716.6665 | 175 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2 | 7.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95.4 | 106 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 87.7333 | 56 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 378 | 54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 389.4999 | 114 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 120 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 22 | 11 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2923.6997 | 507 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1659.7666 | 101 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 373.9331 | 284 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 789.5833 | 125 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1312 | 40 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.75 | 13 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.2615 | 4.11 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.7205 | 5.97 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 175 | 125 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1057.5 | 94 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.8999 | 114 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 48 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1862 | 266 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 429.25 | 101 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.125 | 16.25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.1667 | 14 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164.0833 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 454.4 | 284 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3059 | 322 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.9903 | 10.78 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.7402 | 14.27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.6843 | 39.34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 340.6 | 131 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59.7916 | 143.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.6666 | 40 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 228.3166 | 133 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 413.7 | 42 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 450 | 45 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 668.1665 | 422 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2202.1665 | 362 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2301 | 177 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4704 | 224 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8387.9998 | 270 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 27 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 75 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 484 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 10.5 | 9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 145 | 29 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 650 | 50 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2233.55 | 131 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1904.85 | 51 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 297.5 | 175 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4140 | 45 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.6625 | 3.99 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.5942 | 14.15 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.3167 | 15.16 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7.8166 | 67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.35 | 33 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 137.5 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 343.75 | 125 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.235 | 6.05 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 447.33 | 114.7 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 700.5833 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20 | 20 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 176.7 | 114 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1092.5 | 19 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3434.6666 | 224 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4549.6 | 242 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 624 | 13 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 2 | 1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5900 | 100 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 920.55 | 51 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.272 | 14.58 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.6897 | 16.06 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.5 | 75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 63 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.161 | 16.74 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105.2333 | 77 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 338.8 | 77 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 378.6666 | 284 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1306.25 | 475 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.2083 | 29.05 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98.2666 | 88 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1123.2 | 144 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 308.2 | 46 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 80 | 20 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.4 | 26.7 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.5 | 45 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 512.2333 | 121 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12924.1666 | 50 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 270.9332 | 254 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321.75 | 195 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 564.9999 | 150 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1065 | 355 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.2666 | 56 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.9999 | 90 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 575.7332 | 254 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3441.2666 | 82 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 11 | 11 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 54 | 18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 12 | 12 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 45 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 229.5 | 8.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 24.9 | 8.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 45.5 | 9.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 152.805 | 18.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 51.9 | 17.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 79.91 | 18.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 73.2 | 18.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 83.7 | 9.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 62.9417 | 8.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 77.7 | 11.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 17.2 | 4.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 221.35 | 23.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 180.9 | 20.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 436.3332 | 170 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 557.0833 | 175 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132 | 33 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69.25 | 15 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1240.1666 | 70 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 502 | 251 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 650-Fluidized Bed
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 167.65 | 21 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.6666 | 40 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 239.3333 | 40 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9027.6666 | 146 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 158.3333 | 25 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 650-Fluidized Bed
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 219.5 | 30 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 650-Fluidized Bed
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 84 | 21 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 800-Miscellaneous
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 8 | 12 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 261.3333 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276.25 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 279.5833 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 494 | 65 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 608.9999 | 90 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4874.5833 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5253.3331 | 320 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 177.3333 | 80 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 450 | 9 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.5 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.4166 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 308.2666 | 34 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 397.1 | 418 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 680 | 340 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1029 | 140 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1415.5 | 190 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 906 | 72 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16393.3332 | 400 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.75 | 87 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.25 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.5 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 194.25 | 111 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 633.3333 | 95 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 108.64 | 38.8 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 176 | 16 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1066 | 26 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 130.5 | 290 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 220 | 220 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 251.1667 | 22 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 304 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1367.9998 | 270 | 2 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1914 | 330 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2067.9998 | 330 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4490.1666 | 290 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13475 | 220 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 25.2 | 5.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 4.4166 | 53 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.06 | 49.8 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4992.5667 | 38 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.4 | 48 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.3333 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.8333 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.9999 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 375 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 547.5 | 75 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 201 | 33.5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230.9999 | 315 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 854.1667 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.5 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 314.9998 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 363.1333 | 52 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 486 | 54 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 695.8333 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 706.9999 | 420 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 728.5 | 93 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1508.3333 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2979 | 54 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3971.4999 | 390 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8999.1 | 303 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 341.6666 | 100 | 2 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 198 | 33 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26 | 39 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.1666 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 161.6667 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 167.9999 | 144 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 245.8332 | 250 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 263.0833 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 365.5 | 170 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 662.5 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1815 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47121.05 | 89 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89.3 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108 | 18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.96 | 14.44 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 165 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.3333 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125.7999 | 204 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 266.2 | 44 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 308.3333 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 604.75 | 59 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1053 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1331.8332 | 262 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1790.8 | 242 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3890.1332 | 448 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3957.3331 | 320 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5944.9998 | 300 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 14.8 | 7.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 0.66666 | 4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 3.0333 | 13 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 244 | 122 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1200 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160.5 | 90 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 868.21 | 47.1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 230.9999 | 90 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.75 | 75 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.6667 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 528.4499 | 117 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165.8333 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 217.6 | 17 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 316.3332 | 260 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 595.9999 | 240 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 600.3 | 54 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 695.9999 | 360 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 929.4999 | 195 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1022.8998 | 318 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1078.5832 | 215 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2275 | 260 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17420.3333 | 220 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.6167 | 45.5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 750 | 50 | 1 | 2 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4642.9166 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.8333 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.95 | 33 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 277.9166 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2338 | 167 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4147.5 | 79 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1862.9332 | 224 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 154.7 | 51 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 832 | 320 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1051.4582 | 257.5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15926.6664 | 400 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18251.8832 | 251 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 215 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 181.3333 | 160 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 491.6667 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 337.5 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 350 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450 | 50 | 1 | 2 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2271.5 | 35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8194.635 | 90.9 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.5 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71.4 | 51 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.5 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.15 | 17 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 152.65 | 71 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 90 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369 | 135 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 424.6666 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1810.0833 | 107 | 2 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1929.6666 | 140 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2131.4999 | 126 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.6666 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 240 | 16 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 715 | 39 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4618.25 | 203 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 73.65 | 9 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 209.9999 | 360 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270 | 54 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 317.4054 | 268.23 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 480 | 240 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 662.8331 | 410 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 934.4332 | 194 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1314.4999 | 330 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1349.95 | 133 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3191.7498 | 255 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 43.24 | 27.6 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 10850 | 350 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 144 | 72 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 170.8 | 84 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140 | 35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.9999 | 75 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198.6667 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 301.5833 | 35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 412.5 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.6667 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 276 | 46 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 311.6 | 114 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 352 | 16 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.75 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 217.5 | 290 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 330 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 601.1999 | 108 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1406.4665 | 292 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1825.95 | 47 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2109 | 190 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2255.7666 | 118 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5134 | 128.35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 24 | 3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2770.8331 | 350 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.5833 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.0833 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1438.8 | 36 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 800-Miscellaneous
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 5132.75 | 419 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1583 | 395.75 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 8.4 | 9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 40.7167 | 7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 147.6333 | 17.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 0.4 | 0.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 10.9947 | 10.64 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 196.6666 | 59 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 134.49 | 44.83 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 204 | 20 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 469 | 16.75 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 16.7265 | 17.01 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 47.3 | 17.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 97.86 | 32.62 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 2.7333 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 0.93333 | 1 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 6.25 | 5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 17.2 | 17.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 254.919 | 38.43 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 4.1 | 2.05 | 1 | 4 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 10.25 | 2.05 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 54.06 | 18.02 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 21.7066 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 0.68333 | 1 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 243.25 | 35 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 19.8333 | 5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 75.95 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 2.05 | 2.05 | 1 | 3 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 12.3 | 2.05 | 1 | 2 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 18.45 | 2.05 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2.35 | 3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 3 | 5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 4.05 | 9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 6.3 | 6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 80 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 89.01 | 29.67 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 93.03 | 13.29 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 8.2 | 2.05 | 1 | 2 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 19.3 | 19.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 49 | 30 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 72.3667 | 13 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 94.6666 | 40 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 106.3333 | 22 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 7.8667 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 9.7333 | 8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 10 | 12 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 12.95 | 7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 11.5493 | 5.68 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 16.4 | 2.05 | 1 | 2 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 2678.4 | 37.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 14.08 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 15.86 | 7.93 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 7.2667 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 451.08 | 225.54 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 11.55 | 11 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 12.2 | 12 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 69 | 23 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 129.3 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 6.15 | 2.05 | 1 | 3 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 59.45 | 2.05 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 14.5 | 14.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2.8667 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 9.9 | 6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 117 | 7.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2871 | 220 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 34.7013 | 20.02 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 191.2533 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 3485.3866 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Summer | 51.3333 | 11 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 14.4 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 78.2167 | 13 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 61.3333 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 21 | 28 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 28 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 58.2667 | 8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 150.7333 | 28 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 23.78 | 11.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 944.1667 | 25 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 8.125 | 7.5 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 9682.2 | 66 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | U1-Forced - Immediate | 800-Miscellaneous
0113 | Solid fuel tank/hopper fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 28.7 | 4.1 | 1 | 1 | 0113-Solid fuel tank/hopper fires | D1-Forced - Immediate | 650-Fluidized Bed
0113 | Solid fuel tank/hopper fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 38.7 | 12.9 | 1 | 1 | 0113-Solid fuel tank/hopper fires | D1-Forced - Immediate | 650-Fluidized Bed
0113 | Solid fuel tank/hopper fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 180 | 12 | 1 | 1 | 0113-Solid fuel tank/hopper fires | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8.4 | 4.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.9 | 3.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12.3 | 4.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 13.2 | 4.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 28.4 | 7.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 39 | 3.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 126.7 | 18.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 11.1 | 3.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 90 | 9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10.5 | 3.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 22.4 | 1.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 24.3 | 8.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 37.8 | 5.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 58.5 | 3.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 76.8 | 9.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 201.6 | 14.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 5.2 | 5.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 38 | 3.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 40 | 5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 72 | 8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.4 | 3.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 4.2 | 1.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9 | 1.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 14.3 | 1.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 25.2 | 6.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 33 | 5.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 38.4 | 12.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 44 | 11 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3 | 1.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.8 | 3.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8.8 | 4.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 58 | 5.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 78.2 | 4.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 18 | 3.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 23.8 | 3.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 11.4 | 3.8 | 1 | 2 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 14 | 3.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 15.6 | 5.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 22.4 | 3.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 90.3 | 12.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 358.4 | 25.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.2 | 3.2 | 1 | 4 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 17.8 | 8.9 | 1 | 2 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 41.8 | 3.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 13.6 | 3.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 19.6 | 2.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 54.6 | 3.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 57 | 11.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 63.6 | 10.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 259.2 | 10.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4.2 | 4.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 19.2 | 3.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 124.2 | 13.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 1.6 | 1.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 12.2 | 12.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 15.2 | 7.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 59.5 | 3.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9 | 9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 16.8 | 4.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 29.6 | 3.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 79.3 | 6.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 9.3 | 3.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 13.2 | 3.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.8 | 3.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 14.8 | 3.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 0.48 | 0.64 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 13.6 | 6.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 31.2 | 5.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 44.2 | 3.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 50.4 | 3.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 133.6 | 16.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 12.6 | 4.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 21 | 3.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 37.4 | 3.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.6 | 3.6 | 2 | 3 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6 | 2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 31 | 6.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 43.5 | 8.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Winter | 205.15 | 16.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 800-Miscellaneous
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 176.3333 | 20 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 8.9333 | 4 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 106.8 | 18 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 14.3333 | 5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 1413.8666 | 88 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 0.58333 | 1 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 10.6333 | 11 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 57.3333 | 20 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 71.6 | 24 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2.7 | 3 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 3170.2166 | 67 | 1 | 1 | 0116-Solid fuel feeder motors | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 12.5 | 12.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.8608 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.68 | 4.68 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 12.1075 | 5.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 21.8533 | 4.4 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 126.17 | 4.65 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 10.25 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2171.6923 | 9.29 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2886.5097 | 7.78 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 187 | 37.4 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.6417 | 1.97 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.5375 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.8903 | 2.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.7 | 6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.329 | 7.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 8.2125 | 3.65 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 4.1 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 17.738 | 1.81 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 86.6667 | 50 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 21.5708 | 8.35 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 31.185 | 4.86 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 127.1912 | 9.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.8348 | 1.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2.34 | 2.34 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 5.1133 | 5.2 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 19.8633 | 20.2 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 9 | 54 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.5563 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.827 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.62 | 5.04 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 12.2243 | 4.34 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 48.12 | 8.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 224.025 | 29.87 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1.3533 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 6.15 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 403.526 | 10.68 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 100 | 50 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 37.5 | 50 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 1007 | 100.7 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.7152 | 2.51 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 9.375 | 7.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 11.65 | 6.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 16.287 | 8.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 178.4213 | 3.89 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 11.305 | 7.98 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 5.2065 | 2.67 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 47.6303 | 9.59 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 717.068 | 5.16 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1399.848 | 8.46 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 18.9 | 54 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 21.875 | 12.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 27 | 27 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 30 | 6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 646 | 80.75 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 822 | 68.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.897 | 4.98 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 7.743 | 2.67 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 402.5 | 8.4 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 9.4 | 9.4 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.9623 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.5467 | 1.76 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 6.231 | 4.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 14.1397 | 5.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 20.9132 | 7.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 24.9792 | 11.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 968.579 | 4.82 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 12 | 6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 2.05 | 2.05 | 1 | 7 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Winter | 20.5 | 2.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 254.3307 | 11.09 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1320.538 | 7.22 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 33.3 | 54 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 27473.6 | 312.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 42 | 42 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1.9043 | 1.97 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.1315 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.9923 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.9363 | 2.51 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 8.2043 | 3.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 71.4083 | 9.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 0.77817 | 2.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 82.3333 | 26 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2957.9999 | 180 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1818.75 | 125 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2178.8332 | 170 | 1 | 1 | 0125-Coal crusher dryer hammers | D2-Forced - Delayed | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 379.0743 | 125.66 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3521.5625 | 143.25 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 542.97 | 120.66 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D2-Forced - Delayed | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 790.323 | 120.66 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.5 | 5 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1068.375 | 123.75 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2757.7083 | 76.25 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7295.75 | 385 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | U1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4762.9167 | 35 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65.33 | 130.66 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1060 | 120 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2527.6875 | 228.75 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.9999 | 120 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D2-Forced - Delayed | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2096 | 160 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D3-Forced - Postponed | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.3333 | 5 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 178.6666 | 80 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 7 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 14 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.9833 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1524.9999 | 300 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2392.5 | 110 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.803 | 20.73 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 3 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.1 | 19 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1179.3498 | 309 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3994.6665 | 280 | 1 | 1 | 0129-Other coal processing system problems | D3-Forced - Postponed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.6 | 42 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.7917 | 27.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.6833 | 133 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 372.0166 | 101 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18831.96 | 148.4 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.05 | 31.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 662.8666 | 163 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.25 | 5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88 | 22 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44 | 55 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.79167 | 0.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2597.16 | 18.4 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7848.5 | 55 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 625.6599 | 172.2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43.75 | 37.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.6667 | 17 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 457.3332 | 280 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1129.1166 | 37 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1312.5 | 350 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 150 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 588.5833 | 35 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1376.6665 | 350 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 320.01 | 106.67 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.0625 | 0.75 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.3333 | 0.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.0833 | 85 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.8329 | 138.42 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60.6667 | 20 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 389.6667 | 20 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 615.75 | 45 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 143.25 | 45 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 73.2333 | 13 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 887.04 | 40.32 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 184.98 | 30.83 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0140 | Sorbent handling screens | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 97.35 | 33 | 1 | 1 | 0140-Sorbent handling screens | D1-Forced - Immediate | 650-Fluidized Bed
0156 | Other sorbent feed problems | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 114.7 | 37 | 1 | 1 | 0156-Other sorbent feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 860.95 | 67 | 1 | 1 | 0163-Bed material feeders | U1-Forced - Immediate | 650-Fluidized Bed
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255.6666 | 118 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8072.9166 | 125 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720 | 20 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 524.3333 | 52 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1143.3333 | 56 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20231.25 | 325 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 776.3333 | 34 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 324.5 | 22 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110 | 20 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14955.85 | 173 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | U1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1545 | 36 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 113.9 | 34 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1251.2 | 34 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2893.3333 | 80 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235 | 20 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30 | 12 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26480 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 366.5833 | 83 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6154 | 30 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1874.1666 | 65 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116.6667 | 50 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 284.8 | 24 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 715.7333 | 88 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 456.7333 | 34 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 589.3333 | 52 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10752 | 70 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 166.6 | 34 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 803.1 | 18 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 331.8331 | 362 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | U1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 819.8666 | 52 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2498.9666 | 61 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 222.6666 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17368.05 | 139 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 61.25 | 35 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.5833 | 5 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.25 | 15 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 910.5666 | 118 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 222 | 60 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1032.2 | 39.7 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 33.3667 | 7 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.0833 | 59 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.9999 | 87 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.0333 | 14 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.3333 | 40 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.5 | 63 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 338 | 169 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0210 | Pulverizer heater (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.9666 | 91 | 1 | 1 | 0210-Pulverizer heater (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0220 | Pulverizer system cyclone separator | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 572.4999 | 150 | 1 | 1 | 0220-Pulverizer system cyclone separator | D1-Forced - Immediate | 100-Fossil-Steam
0230 | Pulverizer bag filter | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 340.6666 | 140 | 1 | 1 | 0230-Pulverizer bag filter | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43 | 86 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.1666 | 70 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.0666 | 167 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.5 | 45 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1067.1664 | 337 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1376.0832 | 337 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10710.7 | 64.2 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57.3333 | 80 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 722.064 | 110.52 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20 | 20 | 1 | 1 | 0240-Pulverized coal bin | D2-Forced - Delayed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 892.1666 | 101 | 1 | 1 | 0240-Pulverized coal bin | U1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.8333 | 110 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 282.75 | 377 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 481.4333 | 202 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11480.3333 | 62 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 123 | 41 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 288.8 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1519.98 | 253.33 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 565.2497 | 399 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 588.75 | 157 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 813.1666 | 287 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64.0666 | 124 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 226.4999 | 90 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180.8333 | 217 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198 | 132 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.1665 | 202 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 308.75 | 247 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 908.4999 | 237 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.6666 | 140 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 157.7 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 212.7999 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 53.3333 | 50 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 325.4766 | 51.8 | 1 | 1 | 0240-Pulverized coal bin | D2-Forced - Delayed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65 | 100 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 738 | 164 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32.4999 | 78 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.2 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 207.0999 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1230 | 75 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205 | 164 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1224.0665 | 244 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 184.2999 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5833 | 59 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 138.3333 | 166 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1405.2499 | 219 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4335.5 | 290 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 117.5 | 94 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 271.0333 | 94 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 408 | 272 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2717 | 190 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 117.8 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 376.6667 | 20 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 427.5 | 90 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.6833 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.8 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.2 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.9667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.1 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.2 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.875 | 22.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.6833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.25 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.1499 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.8666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.3333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.7999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.7 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.1333 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69.3499 | 219 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.9 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77.55 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.1 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 110 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117.3332 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 134.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.4 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163.8 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 169.3999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.75 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.8 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 218.5 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 278.0323 | 43.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 308 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 308 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 322 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 410.7499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 418.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 550 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 610.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 690 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 691.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 754 | 232 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1022.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1203.2 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1413 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1474.9999 | 177 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1876.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3148.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3274.5 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18554.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.4666 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.8333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.75 | 34.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.9 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.8333 | 29.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.4833 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.2666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.8917 | 45.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.1333 | 44 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.15 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.75 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.3 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.601 | 44.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.9166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.6333 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.3 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63.4666 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.5333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.3 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.0866 | 58.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.7997 | 378 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 103 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116.45 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.5999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.7549 | 135.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.8333 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.3499 | 153 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 228.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 260.7 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 263.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 273.7999 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 294.2333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 322.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 471.4399 | 199.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 513 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 634.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 774 | 258 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 795 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 867.4333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 942.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1162 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1299.3165 | 259 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1310.3116 | 59.65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1429.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2398.9333 | 208 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12659.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.25 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.1333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23 | 23 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.8 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.6333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.44 | 69.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.529 | 74.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.5333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.6 | 50.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.35 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 65.7 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68.5666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 87.915 | 58.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 120.3331 | 380 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 121.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 128.8 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 136.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 169.85 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 177.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 190 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 200.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 246 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 248.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 255.3833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 261.8825 | 146.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 265.375 | 42.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 292.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 348.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 360 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 418.5 | 279 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 436.8 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 464.6664 | 340 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 485.9166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 517.65 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 585.9333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 624.1665 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 720.1 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 814.7333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 830.5 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 874.3332 | 215 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1076.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1226.7 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1339.9998 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1492.09 | 26.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1632 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1705.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2070 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2088.45 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3010.5 | 223 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5667.5167 | 48.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5813.3332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.4 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 50 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 88.45 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 124.6 | 356 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 130 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 166.3666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 214.2 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 235.85 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 248.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 319.467 | 76.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 358.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 360 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 394.35 | 131.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 880.3998 | 372 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.1833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2025 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.3 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Winter | 53.0099 | 167.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 54.6 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 141.7833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 163 | 81.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 525 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1184.96 | 148.12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1513.05 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179 | 35.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.22 | 109.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.3 | 18.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.7 | 62 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.8 | 20.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 664.36 | 20.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 49.5833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 77 | 12 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1250.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1988.6666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 150 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 254.15 | 51 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 355.2666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 416 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 457.7 | 69 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 703.5 | 210 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 163.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 358.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 248.3999 | 162 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 748.7166 | 167 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31203.4998 | 510 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.75 | 63 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 181.7333 | 232 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.2167 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.7333 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.9667 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.445 | 38.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.75 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.5583 | 90.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.85 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.68 | 43.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.8167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.05 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.0832 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.5999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.5833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.3833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.9999 | 420 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 99.3999 | 213 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.0666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 121.6666 | 100 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.3333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165.6 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 186.55 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 189 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 194.75 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201.7167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 212.6666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225.15 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 228 | 380 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 234.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 237.9999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 265.02 | 151.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 282.1333 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 289.0683 | 69.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 298.1555 | 55.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 298.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 307.8 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 337.5 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 371.3 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 375.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 413.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 425 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 438.1332 | 212 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 483 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 501.1666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 505.3 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 545 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 550.6666 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 588.4806 | 66.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 807.3 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 841.5 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 897 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 904.4 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 951.4999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1037.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1044.94 | 80.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1379.9999 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1609.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1644.9849 | 114.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1684.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1695.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1715.4 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2286.9332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3759.9996 | 600 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.8 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.1167 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.3667 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.4667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.2 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.9833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.8666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.6 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.9666 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.3 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.0417 | 33.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.3666 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66.5833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.0833 | 115 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.7333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87.4999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 91.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 106.0666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117.2499 | 201 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.9999 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.2 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154.6666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 163 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 177.8333 | 97 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 188 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 208.26 | 140.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 223.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 239.2 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 266.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 289 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 312 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 312.3843 | 112.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 441.75 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 449.55 | 333 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 480.5333 | 108.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 604.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 629.3333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 655.5 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 962.4999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1024.8333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1062.5 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1072.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1081.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1245 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1578.8983 | 117.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1629.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1824.6666 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1906.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2687.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3465 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.9833 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.3 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.415 | 36.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.5 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.6333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.2333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.9175 | 99.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.6 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.2333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.6667 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51.5666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 58.25 | 233 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 66.55 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.6366 | 69.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 89.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.2667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 102.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.1666 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 115.7166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 154.17 | 16.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 163.3331 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 177.8667 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 196.2 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 202.0167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 210.7333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 220.0833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 228 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 234 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 300 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 301 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 339.45 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 372 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 382.4998 | 270 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 393.25 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 409.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 435.1333 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 437.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 446.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 461.0666 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 483.9333 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 583 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 606 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 616 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 682.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 754.35 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 807.4999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 917.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1099.4166 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1619.9333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.8 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.9167 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70.4 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 103.4041 | 95.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 157.45 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 237.9666 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1138.3666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5412 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41.6 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 83.12 | 41.56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 132.16 | 66.08 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 220.15 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 634.02 | 105.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.15 | 21 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.2 | 12.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.725 | 46.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190.6666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1461.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.65 | 33.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 214.1833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 222.6166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 269.4999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 760.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1489.4998 | 270 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.2666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 121.9 | 53 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 191.9 | 57 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 348.4166 | 185 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 149.8331 | 290 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 611.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.8885 | 40.11 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.9666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 546.8166 | 109 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 319.9266 | 64.85 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 809.95 | 167 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.6 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.2666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 11.6667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.3666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.4 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.8 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.8 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21.3333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.4666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.1 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.2 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.0833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.1333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.7333 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.3333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 68.4968 | 36.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.6666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.8333 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.8 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102.3666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.9715 | 80.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 122.8331 | 335 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 139.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 147.3505 | 40.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148.5 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 173.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 200.8499 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216.7169 | 122.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 217.16 | 17.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225.75 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 245 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 271.7 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 280.8 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 282.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.75 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 290 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 303.15 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 315 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 333 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 383.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 398.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 565 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 652.3333 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 672 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 718.9 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 741.1166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 867 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 965.25 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1148.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1192.6 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1206.7999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1535.8333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1542.45 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1556.1 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2220 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2348.8333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2439.9998 | 480 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2983.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3510.8331 | 550 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9290.6666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.93332 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.1667 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.4488 | 40.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.15 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.9 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.2499 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.0666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.75 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.9999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.6 | 129 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.4167 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.35 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.5832 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74 | 74 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.0803 | 64.93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85.8333 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.9333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.6667 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.8 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 149.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160.3 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 164.4 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255.2 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 358.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 361.8799 | 199.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 371.9999 | 279 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 406.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 438.9 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 473.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 508.5 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 513.4999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 514.2499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 570 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 671.3333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 675.7998 | 327 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 728 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 768.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 775.0166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 775.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 921.0999 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 988.0832 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1028.9998 | 315 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1182.7333 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1204 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1468 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1784.1166 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3012.7499 | 351 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4760 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5818.1164 | 361 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10729.5665 | 202 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.0416 | 26.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.6933 | 23.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.015 | 41.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.4 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.24 | 43.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.3667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.3333 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.3333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.35 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 52.6608 | 48.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55.5 | 74 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62.8999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72.85 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 74 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110.55 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 119.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.9333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 187.8332 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 189 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 234.3833 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 243.1998 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 246.9999 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 257.4 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 261.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 263.4373 | 70.88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 278.6875 | 85.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 291.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 294.55 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 295.5166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 326.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 331.5 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 332.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 334.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 400 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 425.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 432.8333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 472.5 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 490.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 811.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 830.8 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1005.75 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1938 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2026.0499 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2172.1 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2569.3332 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3229.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.1833 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.9 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 390 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1273.04 | 159.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.2667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120.4666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 193.8 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 217.5666 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 442.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 547.55 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 102 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 309.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 938.1 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1453.6666 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2136.06 | 118.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2425.92 | 151.62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.175 | 28.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.725 | 26.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.2 | 27 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.2 | 40.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98.4 | 16.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209.45 | 71 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.735 | 31.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.7833 | 19.75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.425 | 24.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 233.8333 | 61 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 284 | 71 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 870 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 277.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1333.6166 | 71 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 176.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 237.9999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 509.1665 | 235 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128 | 24 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 524.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 365.5833 | 107 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.28 | 34.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.8133 | 36.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.3 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.8 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.5 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.39 | 54.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.3 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.2833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.9333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.7499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.6 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 89.8333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 104 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.5 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.566 | 171.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.8 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 144.1055 | 41.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.75 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 182.5333 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 191.1 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225.9186 | 99.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 247.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 283.6666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 297.6666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 359.3333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 372.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 378.25 | 445 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 389.5 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 452.25 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 470.8166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 493.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 503.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 550 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 558.8 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 622.9999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 714.5333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 760 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 833.1683 | 37.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1234.575 | 125.55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1245.777 | 56.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1248 | 312 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1376.6666 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1653.1166 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1781.7333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1812.5 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1868.665 | 101.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3285.25 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10620.6332 | 322 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 3.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.3166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.4 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.5 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.3666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.05 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 15.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.6667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.2667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.9999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.6 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.0833 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.2667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.8 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.1999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.4 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.0833 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.85 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 49 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.8666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76.4166 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 109.2833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.4 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117.5333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 125 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129.95 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.2666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143.1333 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.4666 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.6666 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 187 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 234.3666 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 245 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 249.6666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 258.75 | 207 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 269.3333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 276.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 281 | 140.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 288.2 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 301.7333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320.3999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 335.975 | 66.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 385.6665 | 178 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 388.5 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 403.85 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 414.3999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 450.0666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 466.0266 | 108.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 480 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 541.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 581.5666 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 613.4666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 613.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 711.9998 | 267 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 719.3331 | 332 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720.7999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 728 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 749.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 750 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 755.7663 | 553 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 980.4999 | 222 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1090 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1287.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1712.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1800 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1830.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1833.1666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4560 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4596 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.36667 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.45 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.7333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.2 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.1666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.3333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.1167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.5 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.1 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 46.8667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.8333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 65.4478 | 58.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 66 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80.5 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 85.4998 | 270 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89.1665 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 101.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 113.0999 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.3 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114.1333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 119.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121.9166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.1166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.6 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 133.3 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141.6 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 142.4833 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 161.9499 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 174.2 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 190.4 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 198.45 | 37.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 201.6666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 251.6 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 322 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 346.5 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 356.2666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 385 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 389.4999 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 420.9333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 611.6 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 629.3332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 685.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 740 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 933.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1080 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1851.4333 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4717.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 7.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.7333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.5833 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105.6 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 119.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 125.8666 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 264.0333 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 344.96 | 92.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 568.7666 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 826 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2208 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2549.82 | 121.42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 158.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 184.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 74.4333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 639.1 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.5533 | 20.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.9 | 1.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 922.5 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.45 | 33.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.56 | 29.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.8 | 23.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 344.6166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.937 | 11.49 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.2 | 12.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1320 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1165.0832 | 155 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1262.25 | 297 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.8332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63 | 54 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.2 | 33 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1493.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3 | 20 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 478 | 120 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5984.3332 | 260 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.6 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.99 | 46.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.675 | 15.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.4667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.9 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.6667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.8833 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.0417 | 27.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.3666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.9173 | 16.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.9666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.1666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.5 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.4667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.8 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.35 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 65.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69.0666 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.5136 | 90.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.8 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.8667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103.2 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 114.7833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 117 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 134.75 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162.6433 | 165.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170.3333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 186.75 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.7 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 201.5 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 220.248 | 86.94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 248.0665 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 267.8666 | 160.72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 336 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 358.6333 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 397.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 400 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 402.6166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 432.9 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 545 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 559.9999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 697.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 750 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 774.7 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1033.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1129.3332 | 242 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1190.6666 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1268.1999 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1694.2499 | 405 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2152.5 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2392.5 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2579.2 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7816.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.6983 | 31.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.8666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.2167 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.9 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.875 | 23.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.22 | 46.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.4 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.5666 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.05 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.6 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 44.55 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.1 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.5833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.8 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.635 | 57.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.7833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129.5333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.6 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.1666 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 193.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 194 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 216.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 224.1999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225.25 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.2 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261.9 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 267.3 | 198 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 275 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 309.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 319.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 357.4833 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 390.5833 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 403.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 455.9833 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 485.4166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 488.75 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 580 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 591.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 650.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 664.5333 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 808.2499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 916.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 944 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1105.5 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1156 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1194.75 | 177 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1240 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2067.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6523.7332 | 256 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.6667 | 20 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.225 | 32.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.5 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.3333 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.225 | 31.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.6485 | 22.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.3833 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35.4666 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 36.6795 | 38.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.75 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.2667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 54.6 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.4666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.5 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.5833 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 85 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.5666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 92.5 | 370 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 95.2 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.25 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 103.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 115 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 116.1333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.2 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 124.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 124.5833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 126.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 169.1 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 171.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 182 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 183 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 192 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 202.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 213.5 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 243.8706 | 261.29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 294.9999 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 318.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 351 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 375 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 390.5999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 481.4666 | 314 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 490.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 527.9666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 748.5999 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 806.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 945 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 948.2666 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1206.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3112 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6343.9997 | 480 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.3667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.8666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 100.0036 | 69.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 106.5 | 106.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 132 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 156.5666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 181.8 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 261.4108 | 108.17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 444.55 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 676 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 948.7333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.0333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.2667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.7 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 250 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 153.9666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 159.8 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 192.9466 | 144.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 229.6333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 358.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 525 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 531 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 667.98 | 74.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.7 | 14.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196.1665 | 214 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 402 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.525 | 38.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.2083 | 17.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.3633 | 23.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106 | 12 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 379.1666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 168.7666 | 61 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 184.0666 | 251 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 281.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 503.7 | 69 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 794.3999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2730.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 817.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3485.8666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 757.9 | 53 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2722.5 | 330 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4923.5331 | 598 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.5916 | 79.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.8666 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.4 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.6833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.7566 | 66.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 29.198 | 22.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.1167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.4666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.1499 | 109.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.65 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.8999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.45 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.9666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74.8 | 374 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.4333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.1 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.7499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.5166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.8 | 24.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.6166 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102.5 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.3332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 118.125 | 52.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 121 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127.6833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 136.8833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162.3999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165 | 330 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 173.4 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 185.3999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 241.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.175 | 140.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 266.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270.3 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276.9333 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 304 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 306 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 307.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 354.9499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 395.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 400 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 480 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 505.05 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 506.5333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 612.9666 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 704.5433 | 108.95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 736.5999 | 174 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 831.2498 | 285 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 903.3666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 924.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1018.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1092 | 182 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1221.7332 | 431.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1230.8333 | 211 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1435 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1588.6 | 338 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1692.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1973.3331 | 320 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2468.4 | 374 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2621.5833 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.1833 | 35.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.1667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.28 | 35.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.3517 | 40.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.55 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.7333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.5667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.7 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.4 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.95 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.8007 | 30.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.3666 | 154 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 34.5333 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.9333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.3332 | 370 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.05 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.8333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 55 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.8 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.1999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.9666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.4333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 111.5533 | 115.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.8333 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 173.2666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 184.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220.4333 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 302.9167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 352 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 386.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 440.75 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 458.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 473.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 591.4999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 617.5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 664.2 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 846.8 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1172.3 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1787.5 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3930.6666 | 335 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4127.6 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.0338 | 60.29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.5 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.75 | 23 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.9367 | 48.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.65 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54.384 | 24.72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.485 | 64.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.4 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.0333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.4667 | 39.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.2666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 83.7 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.45 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.8 | 81.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102.4999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 156 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 172 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 271.7 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 278.0666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 281.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 301.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 324.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 325.381 | 141.47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 331.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 438.5833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 520 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 576.46 | 49.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 579.168 | 120.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 586.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 633.3059 | 161.01 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 648 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 715.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 722.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 752.4999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 806.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 852.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 990 | 123.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2493.3333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.0666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.3666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84.3333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 102.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 110.8166 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 129.33 | 129.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159.4666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 188.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 197.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 361 | 90.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 433.71 | 144.57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 612.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 3189.03 | 101.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 196 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 196.4096 | 82.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 204.2726 | 93.56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 552.9755 | 143.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1023.6189 | 281.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 138 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 264.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 389.6 | 97.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 195.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.1517 | 28.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.545 | 50.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.4 | 25.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 489.3166 | 157 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.3142 | 12.29 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105.6 | 24 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 163.3 | 138 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 451.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3585.5666 | 263 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6889.45 | 227 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44 | 220 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 150 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 189.9 | 54 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 627.25 | 39 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 657.4 | 57 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 206.8666 | 107 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 226.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 285.65 | 87 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.9167 | 29 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3138.3331 | 700 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 900 | 300 | 2 | 2 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2605.1664 | 770 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.6 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.1666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.2666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.9333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.8867 | 30.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.2 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.6667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.5333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.4832 | 173 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.0166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.4666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48.3333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.0665 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.2666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.55 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 67.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.1333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88.6832 | 313 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107.1132 | 160.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107.1833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.25 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111 | 222 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.8833 | 91 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129.2499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 139.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 146 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 148 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165.9 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 194.6666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 206.4999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 219.5833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240.8 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 248.2667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 257.0499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 294 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 316.8 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.5431 | 139.07 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 350.9333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 352.8671 | 66.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 412.6001 | 66.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 443.2166 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 467.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 487.3332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 530 | 66.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 569.8416 | 112.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 612 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 628.6667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 696.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 748 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 862.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 891 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1019.3499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1045.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1065.9 | 374 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1410 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1430 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1494.3 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1622.3332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1647 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2327.5 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2574 | 286 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.55 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.4166 | 32.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.3999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.9 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.2666 | 227 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 67.2 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.6816 | 84.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.5 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.67 | 55.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.8333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.1333 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105.4 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.7166 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.25 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 139.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 141.1332 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 148 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.1 | 282 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 179.0666 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 213.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230.8 | 115.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236.6667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 277.9166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325.7999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 343 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385.1332 | 218 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 406.9166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 427.45 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 431.6 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 492 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 495 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 497.55 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 523.1666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 689.6998 | 342 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 758 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 805 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 841.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 875 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 896 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1265.7499 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1303.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1738.3666 | 242 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2887.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3562.5333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5212 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.0667 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.12 | 41.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.2666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.75 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.05 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.6666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.5 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.35 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.2 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29.1667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.5 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.75 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.0833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 52.52 | 121.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.5 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 61.5405 | 58.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65.3333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.1 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 83 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.3833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102.2 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106.8 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 113.0666 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 113.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114.7 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 117.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 125.0833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 139.3333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 166.5 | 370 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 278.7333 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 317.2721 | 113.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 354.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 360 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 366.0666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 405 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 411.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 469.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 540 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 697.6666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 739.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 785.4 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 827.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1155.0467 | 21.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2058 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2247.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2680.4666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 44.72 | 62.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 110.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 350.2999 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 471 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2175.6666 | 305 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37.94 | 37.94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 71.2833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 370.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 550.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1569.96 | 87.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 72.0666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91.2666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 626.4 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 655.5 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 11.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.76 | 34.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.8 | 18.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.8266 | 29.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.7 | 40.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 328 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 429.88 | 195.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 340.3999 | 138 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 452.4164 | 445 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1110.8332 | 215 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1782.2 | 133 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129.8333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.9 | 166 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 341.25 | 63 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 744.8 | 266 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.8 | 176 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.3667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.5667 | 22 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.95 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.3333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.3667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.2033 | 50.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.8333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.1666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.2 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50.9833 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 67.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70.4 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.3 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.8 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.9999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.55 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 123.2666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.7667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 167.4 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168.1 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170.8333 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 177.0666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190.7666 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 191.5333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.5 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 238.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 247.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 248.9 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 250.4833 | 79.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 258.6833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 259.6666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.75 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285 | 285 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 294 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 305 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 316.0999 | 379.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 316.3333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 322 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 330 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 331.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 333.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 335 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 345.4 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 370 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 375.4236 | 99.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 415 | 415 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 420.9666 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 477.9 | 177 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 501.2 | 179 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 546.1166 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 612 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 635.0666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 727.8833 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 778.8 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 833.75 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 879.2 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 880 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1000.5 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1040.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1110.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1164.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2484.8166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4420.9333 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 8269.83 | 196.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.6 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.8666 | 59.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.1667 | 33.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.5499 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.8933 | 52.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42.3333 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.8666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.5 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.76 | 57.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.6333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.1664 | 370 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.6716 | 50.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86.5333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.1 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.6 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 216 | 360 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 303.5733 | 56.92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 317.52 | 141.12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 338.7999 | 363 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392.6665 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 435.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 442.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 455.1 | 44.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 480.6 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 514 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 517.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 518.56 | 22.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 596.7499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 654.9332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 862.4 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 889.5833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 976.5999 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1700.9667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1930.1666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2354 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5975.6666 | 197 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12871.8332 | 295 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.0667 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.8666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.8383 | 37.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.3332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.2666 | 36.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27.4833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.9833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.5833 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.1667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.3 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.7499 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61.1 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.25 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 74 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.1667 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90.75 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.05 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.5 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 119.85 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 138.6666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 150.4666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 167.9 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 168 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 183.6666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 194.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 200.5833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 213.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 249.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 290.4 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 297.85 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 305.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 305.8 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 349.9999 | 375 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 383.7999 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 430 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 454.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 502.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 549.0331 | 362 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 617.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 727.1832 | 161 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 752.5665 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 773.5 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 792 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 844.8 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 922.2499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 995.6167 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1088 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1096.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1297.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1683.4665 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3926 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8580 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28.5167 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 47.84 | 62.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 171.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 182.5167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 192.06 | 64.02 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 196.5 | 98.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 201.5 | 100.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 304.95 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 322.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 511.98 | 170.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 571.56 | 95.26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 726.95 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 797.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 112.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.1333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 136.0333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 413.4332 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1635.0333 | 181 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8.6333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 58.6667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.7333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 258.75 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 268 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 323.75 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 436 | 87.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1704.3125 | 123.95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.5 | 29.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 300 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.2833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.556 | 52.88 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 315 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.355 | 18.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 188.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 351.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 781.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 95.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1716 | 165 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4309.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 515 | 100 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 897.102 | 242.46 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1076.25 | 525 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4510.9997 | 780 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 9.6 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 14.4667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 11.37 | 7.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 207.35 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 22.8 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 101.5 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 53.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 76 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 596.9333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 3571.3333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 616 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 595 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 57.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 35.4166 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 141.6167 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 11.7 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 31.1667 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 690 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 6.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 11.3167 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 419.75 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2.3833 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 12.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 32 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 137.2 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 971.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 6.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 3.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 12.8333 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 61.3333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 63.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 10.6667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 15.95 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 31.8 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 31.6667 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 7.1667 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 385 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 108.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 212.45 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 20.9167 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 8.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 20 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 587.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 98.6666 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 157.0833 | 65 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 840 | 140 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.25 | 15 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.1 | 158 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 159.8333 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 325.8332 | 230 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 733.8333 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 163.965 | 64.3 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 310.65 | 109 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 914.485 | 127.9 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1562.5 | 125 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.75 | 7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153 | 18 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 752.1 | 32.7 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.8 | 3 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96 | 24 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 15 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.3333 | 25 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 17.4 | 87 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 159.1216 | 59.3 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238.3333 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 311.6666 | 55 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105 | 21 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 159.75 | 135 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 189 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 371.5833 | 35 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.565 | 117.9 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.35 | 9 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 128.9167 | 17 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.45 | 99 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.3867 | 7.6 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216 | 108 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 383.3332 | 230 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 551.45 | 41 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 989.3332 | 140 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26 | 4 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.3333 | 40 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 209.3333 | 40 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 20 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.25 | 45 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107.6667 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 281.05 | 21 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 381.3333 | 104 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.7 | 78 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 381.6666 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1120.8332 | 125 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 519.2083 | 73.3 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1914.6666 | 160 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.9333 | 32 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30.5 | 10 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160.5833 | 235 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 9.9167 | 5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 37.5 | 5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 30 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 278.7999 | 246 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 89.1667 | 50 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 212.3333 | 70 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1528.8 | 91 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 90.26 | 45.13 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 290.535 | 83.01 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 267.6666 | 55 | 1 | 1 | 0255-Pulverizer feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.6666 | 70 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 135.7283 | 114.7 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 196.0166 | 154.75 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 169.1666 | 70 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 267.6333 | 114.7 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1590.5066 | 114.7 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.3 | 33.3 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216 | 72 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 179.6966 | 114.7 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1208.4544 | 76.89 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 382.5 | 85 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.4999 | 114 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.5833 | 17 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 569.6766 | 114.7 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2832.2665 | 304 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 310.3 | 62.06 | 1 | 1 | 0255-Pulverizer feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 292.04 | 73.01 | 1 | 1 | 0255-Pulverizer feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46285.8331 | 670 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 414.8316 | 114.7 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.9333 | 38 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.5333 | 28 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 288.85 | 109 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 534.7666 | 263 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3136.5 | 510 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3355.0828 | 815 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44.9999 | 108 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 243.4333 | 109 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 64 | 60 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3 | 60 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66.8666 | 34 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 240 | 240 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.2666 | 101 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.3 | 121.2 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29330.8331 | 577 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 177 | 36 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 670.8 | 104 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 863.0499 | 123 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 329.8 | 68 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D3-Forced - Postponed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1638.75 | 475 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8878 | 193 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.9333 | 14 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 623.5 | 29 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.4667 | 8 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2300.3831 | 353 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.4167 | 35 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.15 | 109 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54.5 | 109 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19464.9 | 713 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 444.6 | 156 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.4 | 141 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 105 | 105 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 267.6666 | 146 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 468.3333 | 100 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 14929.5 | 555 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1617 | 140 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 231.0166 | 167 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 430.2 | 108 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 459.65 | 87 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 884.4 | 67 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 931.5 | 207 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1100 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1914 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5050.333 | 545 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.5 | 27 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187.0667 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215.8331 | 350 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 408 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 693.3333 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1002.8665 | 307 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1054.9333 | 64 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3685 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8108.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 370.625 | 148.25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 521.5 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 952.875 | 157.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2881 | 172 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1635 | 75 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.25 | 45 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 450 | 15 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1210 | 550 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.7333 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.8333 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.5833 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 265.8833 | 53 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 451.1833 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2497.6666 | 147.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11988 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.75 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196 | 12 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 284 | 56.8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 672 | 160 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7018 | 58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1166.1998 | 249.9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1243.3333 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1721.7 | 54 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2127.4 | 11 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2367 | 135 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18565.47 | 119.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 830.3 | 166.06 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 217.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97.92 | 14.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 219 | 18 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 878.9 | 51.7 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 3.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1188 | 18 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3273.3333 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2606.6664 | 340 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 773 | 30 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 636.75 | 45 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.45 | 9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.1667 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.35 | 87 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179.8666 | 71 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.8333 | 67 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1020.8333 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1617 | 98 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 16283.8331 | 410 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.5833 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 564.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 797.15 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.6 | 87 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123.9 | 177 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 268.8 | 96 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 494.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 506.25 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 600 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1049.6666 | 134 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1075 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1901.1666 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5889.5833 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190.3867 | 21.8 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3652.95 | 63 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 342.25 | 37 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1248 | 52 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2250.0831 | 335 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3033.3333 | 125 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4229.3333 | 160 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7724.1666 | 65 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 624.8332 | 230 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 702 | 27 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2193.3333 | 70 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6323.9998 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13746.9999 | 354 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156.2166 | 91 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275.7333 | 11 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 345 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 484 | 11 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 592.5399 | 167.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 660 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2081.5 | 115 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22064.4566 | 114.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 127.09 | 127.09 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 760.1 | 69.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1732.5 | 14 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266.17 | 25.8 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.75 | 55 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 522 | 580 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16812.4164 | 881 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9118.0832 | 385 | 1 | 1 | 0260-Primary air fan | U2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.1167 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.1666 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.8333 | 11 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1544.75 | 167 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1706.8333 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4420.8332 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.8975 | 8.85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.6667 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129.1166 | 61 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 186 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 438.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1170 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2720 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4974.6664 | 364 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.6666 | 320 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.25 | 235 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 346.7916 | 143.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 506.9166 | 276.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3148.7332 | 292 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4255 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2605.3333 | 40 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 875.9 | 57 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 118.9998 | 510 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4161 | 876 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17718.05 | 497 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 283.6167 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 595.9999 | 240 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 677.8332 | 245 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 781.75 | 53 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1207.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.8333 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189 | 108 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 208.4 | 12 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219.2 | 548 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 377 | 26 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 628 | 314 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 688 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1703.2666 | 58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3895.5 | 70 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.6666 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 217.375 | 173.9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 483.1875 | 214.75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 529.2666 | 68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 578.75 | 75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 601.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 720 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2320.185 | 119.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5226.6666 | 320 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 259.2 | 28.8 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1719.51 | 23.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.6 | 9.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 432 | 10 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1347.5 | 27.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 153.3333 | 80 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9273.3333 | 40 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1365 | 650 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3586.1997 | 387 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23465.6661 | 820 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 7.32 | 18.3 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 149.5999 | 102 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 775.8333 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1437.3333 | 160 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2975 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4376.1666 | 70 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6390 | 450 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13766.9999 | 117 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.5833 | 7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 507.21 | 30.74 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 879.1665 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1812.35 | 67 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3633.4 | 37 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8645 | 364 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2200.0999 | 147 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 942.3 | 34.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1039.1333 | 71.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2789 | 30 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.1333 | 62 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170.4833 | 53 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 198 | 440 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204.9333 | 53 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1123.75 | 155 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2921 | 460 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7867.5833 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.2167 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 713 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1131.6666 | 140 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1617.2 | 52 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2112.9167 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5047.864 | 321.52 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19389.3333 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44 | 11 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.8666 | 88 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 528 | 88 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2082.78 | 119.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3022.6 | 68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7874.4 | 68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15480 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38433 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 521.6475 | 63.23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 60 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.1667 | 12.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4300.0666 | 26.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.3333 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15235 | 110 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 585.9 | 65.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26 | 30 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 141.75 | 45 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 650 | 40 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 986.7 | 429 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 175.9332 | 364 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 860 | Co-generator Block | RFC | Off-Peak | 2281.2499 | 219 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 860-Co-generator Block
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77 | 55 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141.1666 | 77 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4939.9998 | 600 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2135 | 140 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2513.9999 | 360 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3370 | 100 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5256.6332 | 358 | 1 | 1 | 0262-Primary air fan lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1210.8833 | 107 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.75 | 267 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5049.9996 | 600 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155.15 | 107 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 157.7333 | 91 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 271.7 | 418 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 763.333 | 458 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107.9167 | 35 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.8333 | 101 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 111.15 | 27 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6292.5997 | 438 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41 | 41 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.0833 | 35 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 227.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 455 | 35 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24118.9999 | 267 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.5 | 45 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 157.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 860.25 | 155 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1326.6666 | 40 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204.6 | 66 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14790.483 | 431 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 946.1497 | 447 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 460 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 864 | 108 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 686.8333 | 65 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 757.1666 | 70 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 119.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 379.1 | 223 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1767.15 | 189 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4132.9165 | 175 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5.1667 | 10 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 543.348 | 402.48 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 479.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220 | 44 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 407.2667 | 41 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1045.3331 | 320 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2536 | 60 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.3333 | 20 | 2 | 2 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 141.05 | 13 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3693.8332 | 370 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 61.8 | 103 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10782.9997 | 492 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.6666 | 34 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 167.4999 | 150 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 290.3333 | 52 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 306.6 | 219 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 417.6 | 32 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 492.5 | 197 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1768 | 208 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.2666 | 82 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 105.3 | 78 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.871 | 121.34 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5054.8165 | 259 | 1 | 1 | 0264-Other primary air fan problems | SF-Startup Failure | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10005.2298 | 565.8 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1523.7832 | 259 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.8333 | 22 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 956.1 | 18 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9043.4166 | 185 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88.8333 | 130 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 832.5 | 222 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 164.8166 | 341 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 217.5 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3231.4 | 302 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1339.5 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4683 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2107.7333 | 52 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5988.1433 | 216.7 | 1 | 1 | 0264-Other primary air fan problems | U2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 312 | 52 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360.15 | 63 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 604.5166 | 83 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 748 | 120 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 215.195 | 57.9 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94.4166 | 55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.5 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192 | 120 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471.75 | 111 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 480 | 120 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 393.75 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 397.5 | 530 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79 | 12 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 277.75 | 55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 359.26 | 50.6 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 301.7333 | 62 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.2499 | 147 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 546 | 72 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1082.75 | 71 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 144.7665 | 202 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3480.2664 | 842 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.8332 | 137 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3801.3998 | 249 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7285.5 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 300 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 886.8 | 18 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 686.6667 | 50 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.7516 | 53.3 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 688.4583 | 40.3 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.1 | 154 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 572 | 52 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 262.6666 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323.3333 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 622.5 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 695.8665 | 307 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1507.3332 | 532 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5623.9999 | 240 | 1 | 1 | 0264-Other primary air fan problems | U2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1086.4 | 194 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 112 | 56 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 600.9266 | 55.3 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 293.9996 | 630 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1758.1333 | 76 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 212.6665 | 232 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9468.2329 | 593 | 1 | 1 | 0265-Primary air heater | U2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1091.6666 | 100 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34986 | 588 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 232.5 | 62 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2496 | 13 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 117790.7999 | 92.7 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 269.1 | 138 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4636.8 | 504 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1009.7998 | 324 | 1 | 1 | 0265-Primary air heater | D3-Forced - Postponed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1359.8331 | 410 | 1 | 1 | 0265-Primary air heater | U3-Forced - Postponed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 370.6666 | 80 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75 | 15 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 291 | 97 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | DI | 650 | Fluidized Bed | RFC | Winter | 177.9167 | 35 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7523.3333 | 100 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2220 | 30 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.25 | 15 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 645.9166 | 115 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 1.97 | 1.97 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 2.03 | 2.03 | 1 | 5 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 4.02 | 4.02 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 8 | 2 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 3 | 3 | 1 | 2 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 10.04 | 2.51 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 3894 | 33 | 1 | 1 | 0266-Primary air heater fouling | U1-Forced - Immediate | 650-Fluidized Bed
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1058.2 | 148 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119.85 | 47 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 466.2 | 155.4 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 946.2 | 315.4 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 199.9998 | 300 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 657.9 | 43 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3836 | 191.8 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 418 | 220 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 455.5166 | 151 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 531.6666 | 145 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 612 | 90 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2391.7499 | 135 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54.6 | 18 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.6667 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.3333 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 114 | 95 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.2 | 21 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 883.6 | 376 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 100 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 266.6666 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 936 | 312 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 218.9166 | 71 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1108.35 | 49.26 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.6666 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 689.2995 | 678 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 76.0666 | 28 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 790.6 | 134 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 287.5 | 230 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 452.6667 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 456 | 152 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1668.3333 | 55 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 699.0666 | 107 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.0833 | 145 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.5 | 39 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.1329 | 668 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 366.6666 | 200 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 168.6665 | 220 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1770.04 | 41.1 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.3333 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1547.55 | 162.9 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3364.5331 | 682 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 635.1 | 87 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 120 | 120 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 278.75 | 75 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2637.4999 | 75 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 172.592 | 75.04 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.8 | 27.6 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13205.5 | 770 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23263.4583 | 160.9 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1163.3332 | 200 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1300.8333 | 175 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.75 | 5 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 791.6665 | 250 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.75 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.9166 | 95 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.5833 | 115 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 208.6667 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 825 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.3333 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 47.544 | 135.84 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.34 | 19.6 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 248.5 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 876.375 | 10.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1950 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3070 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29 | 29 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 53.4533 | 84.4 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 109.3333 | 32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1694 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 739.7333 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220.4 | 87 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 165.75 | 51 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3676.6166 | 239 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 252.6333 | 53 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 83.7 | 31 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 233.1333 | 26 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2614.4162 | 685 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23299.9372 | 498.75 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 268.299 | 141.21 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 425 | 68 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 802.5333 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1016.75 | 49 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8532.3332 | 179 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 526.1666 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 644 | 105 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2822.9332 | 134 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 136.8 | 684 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1243.6666 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1683.5 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2015.0666 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 216 | 6 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 248 | 32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 416 | 8 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1575 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.6667 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 600 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.25 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.8333 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 846 | 564 | 1 | 1 | 0270-Primary air duct and dampers | SF-Startup Failure | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13086.1332 | 496 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.3333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.8333 | 46 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108 | 72 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.995 | 146.22 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 443.3333 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 233.9999 | 108 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6190 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.8 | 24 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 154.0833 | 43 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 343.85 | 69 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3916.7999 | 108 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 176 | 16 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.98 | 12.4 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.2666 | 58 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 98.9333 | 16 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1320 | 132 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 269.1 | 299 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.5333 | 59 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.3167 | 23 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197 | 197 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 816.6666 | 245 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1400 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1570.1382 | 149.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.9999 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 175.3333 | 105.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 312.75 | 139 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 328.95 | 129 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.15 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 210 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 374 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 634.4666 | 124 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 832.1329 | 632 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4012.8 | 66 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 510 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1440 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.6667 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.5 | 66 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 440 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 573.5 | 74 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 255.5 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17041.65 | 489 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82.61 | 75.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 170.8333 | 205 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 361.6666 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67.5 | 150 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 131 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 720 | 240 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2227.5 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9502.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 0.71664 | 43 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 201.2499 | 105 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 664.4625 | 29.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 756 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5765.4999 | 78 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8504.4499 | 111 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.75 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3213.2083 | 115.1 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.7667 | 47 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 152.95 | 69 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 195 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81 | 12 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287.1 | 58 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 330.9332 | 146 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 446.2 | 194 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.45 | 3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.1 | 6 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.9 | 19 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 83.9166 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 339.25 | 69 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552.9333 | 88 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290 | 145 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 653.3333 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 742.9 | 138 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 47.6 | 136 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.8 | 87 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.6667 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.9166 | 215 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 253.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 221.95 | 69 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8288.4 | 36 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.9166 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 174.5999 | 108 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 246.5 | 145 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 783.9999 | 168 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1804.1998 | 279 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8352 | 174 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68.85 | 81 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105.3333 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4974.1667 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29.7917 | 5.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46 | 69 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.5998 | 104.83 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 195 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 625 | 125 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1075.4333 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1745 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3660.8665 | 617 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 216 | 72 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3552 | 37 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.1333 | 56 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.6667 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.4666 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4506.8 | 114 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 319.2166 | 107 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 457.25 | 155 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.3 | 78 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 176.85 | 131 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 268.4 | 244 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 379.5 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1029.1666 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.6667 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.4 | 12 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1228.3333 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 79.75 | 5.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1135.3333 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 210 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8990 | 145 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 100.3332 | 215 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49 | 21 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.65 | 129 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 149.9586 | 160.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 212.3333 | 49 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 806.9999 | 90 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1376.4062 | 160.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2415 | 140 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2654.6666 | 110 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2916 | 54 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3645 | 180 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 135 | 90 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 119.5166 | 71 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160.1666 | 62 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 600 | 150 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 713.2358 | 174.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1646.6666 | 130 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 966 | 69 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6968.75 | 75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7075 | 250 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8433.75 | 195 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.95 | 9 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.608 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81.1151 | 66.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 199.4666 | 64 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 381.25 | 75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1876 | 134 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.89 | 47.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153.9915 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3615.3333 | 88 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 630.6666 | 110 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.115 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 352 | 44 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2772 | 240 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.6667 | 13 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 550.9999 | 174 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 723.3332 | 155 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.85 | 9 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 426.5999 | 81 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 576 | 192 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 857.375 | 451.25 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2287.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6510 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.5 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.9166 | 203 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.5 | 75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1230.8333 | 35 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1485 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1970.25 | 71 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2723.9999 | 144 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6216.6666 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.4666 | 73 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 107.1132 | 160.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 179.1667 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290.3333 | 65 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 292.125 | 42.75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 435.5 | 65 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 7.0833 | 5 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1430 | 130 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.2 | 31 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3333 | 19 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.6 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62 | 62 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 568 | 71 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 596.05 | 91 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 630.5 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 733.3333 | 110 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 804.6666 | 71 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.3333 | 20 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.8666 | 92 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2584.6166 | 79 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110.7166 | 73 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 184.8 | 48 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 906.5 | 49 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5059.75 | 111 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210.7333 | 58 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 974.6666 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1346.6665 | 323.2 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35928.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.55 | 433 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 351.3333 | 62 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 926.8999 | 138 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 262.9 | 33 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 74.8125 | 498.75 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 825 | 150 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1282.5 | 135 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1578.66 | 95.1 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78 | 24 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2017.1333 | 79 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 257.3951 | 136.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152.0832 | 125 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 860 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.3667 | 29 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.3333 | 14 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.7167 | 19 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1042.0166 | 103 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1115 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2890.7 | 211 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.6833 | 29 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.5833 | 85 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 322 | 28 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 420 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540.1667 | 35 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1536.5333 | 43 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 188 | 94 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246.6333 | 49 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 978.75 | 45 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22050 | 175 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1476.3333 | 20 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.2667 | 16 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.6333 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.0667 | 16 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 118.15 | 51 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 169.4 | 66 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 232.5 | 31 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 248.4 | 72 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 270.7833 | 11 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 549.4 | 67 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1091.9667 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1160.4666 | 52 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 814 | 74 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.7499 | 105 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.4667 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87.1 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133.4 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224 | 112 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 710.6 | 68 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 785.15 | 41 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1295.8 | 22 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5755 | 30 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7953.3332 | 200 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28 | 7 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60.45 | 31 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 149.8333 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 155.5667 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 204.0833 | 31 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 224.6333 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 329.6333 | 62 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 409.6833 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1127.2167 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3228.9 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 360 | 80 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 494.5 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8793.3333 | 50 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.1667 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98.1333 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 429.9166 | 67 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2840.0832 | 197 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2954.3333 | 20 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66.5833 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.9333 | 16 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.5167 | 41 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 223.9999 | 192 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 299 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 411.25 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 588.75 | 157 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 667 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 680 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 961.9333 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 262.9 | 33 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3603.15 | 27 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66.6666 | 80 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108 | 36 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200.4166 | 37 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 312.0333 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 407.3333 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450 | 100 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 566.3667 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 575 | 115 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 581.35 | 77 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 614.7166 | 77 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5580 | 150 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12435 | 150 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24692.5 | 50 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37256.25 | 125 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42000 | 150 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14089.8333 | 130 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.6 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56 | 14 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.3333 | 37 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 101.8333 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 214.4 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 287.5 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 617.2667 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 701.8667 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.1667 | 11 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.7 | 41 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 305.1333 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 471.9 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1153.6 | 112 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1649.3166 | 67 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3239.0833 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4661.0666 | 112 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6394.3333 | 20 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.8667 | 16 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 179.8333 | 65 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 293.6333 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 319.8 | 52 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 440.0666 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 851.7666 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1007.3 | 42 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1184.4 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1739.5666 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.5 | 30 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44 | 12 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.5833 | 17 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 347.0167 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 487.9833 | 67 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 527.9167 | 35 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 561.15 | 87 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 782.1 | 237 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 791.1667 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1788.7999 | 192 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3657.6999 | 237 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2882.3333 | 20 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 45 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.15 | 39 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.5 | 42 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.1333 | 11 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 112.8 | 36 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 247.6333 | 17 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 612.7333 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 750.2 | 66 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3383.2167 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.8333 | 50 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.25 | 61 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.25 | 51 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 245 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 248.2666 | 266 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 507.0833 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 614.1 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 819.4666 | 112 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1914.4667 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2844.2833 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12356.3 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90 | 36 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1733.0833 | 35 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.5666 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.2 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130.2 | 21 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220.9 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 245.8667 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 275.3833 | 31 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 374.1333 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 469.8667 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 664.2667 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 667.8 | 53 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1046.5 | 42 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1762.2 | 66 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2426.6666 | 52 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 68.2667 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 194.3333 | 20 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.5833 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 281.3666 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 311.9166 | 197 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1000.5 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1186.8 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1317.1667 | 10 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1395 | 31 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1936.4 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2177.6667 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2888.8 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4673.3667 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8744.75 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8832.4999 | 150 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10928.0332 | 137 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.5 | 7 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.55 | 31 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82.1333 | 32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.5 | 11 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 189.8 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 224.8167 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 438.5333 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 839.5 | 46 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1299.55 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2964 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15125.5833 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.55 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 42.55 | 37 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 850-Combined Cycle Block
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147.2166 | 121 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 306.9 | 9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 539.6 | 114 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6767.4999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.6667 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.5 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 175.95 | 69 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 725.3333 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 376.8783 | 6.1 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3773.9999 | 180 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 462.5 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6555 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1321.4016 | 59.3 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1655.85 | 57 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1229.9999 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5980 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1760 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4062.6666 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1999 | 78 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78.2 | 68 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 132.726 | 120.66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 487.6666 | 76 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 666.6 | 99 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 868.0833 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1693.25 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 331.5 | 51 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 482.05 | 93 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 984 | 96 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15096 | 296 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 938.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1973.9999 | 180 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3210 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10950 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1.8333 | 5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246.1666 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 623.4666 | 56 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1470.5 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1696.5 | 58 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4254.9999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102.0625 | 53.25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135.7908 | 34.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 255 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 416.6666 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 500.25 | 115 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 533.25 | 81 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1606.1583 | 48.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4280.5832 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 150 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 53.2833 | 23 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 401.4999 | 165 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3266.5 | 235 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1389.2333 | 142 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8131.8332 | 194 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3683.4999 | 417 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.6666 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190.6333 | 86 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 213.3333 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 762.1666 | 170 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 763.0666 | 194 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 952.5 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1837.5 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.3333 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.4167 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1340.1333 | 46 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1690 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 388.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 613.3333 | 115 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 685.85 | 87 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 896 | 64 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1034 | 235 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1416 | 96 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2344 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 532 | 76 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83.75 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168.4166 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1049.3166 | 167 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1981.6666 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3060 | 180 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.5333 | 32 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39 | 18 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.4 | 88 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 269.01 | 89.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 329 | 47 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 405 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1325.94 | 94.71 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1338.25 | 101 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 172.6666 | 140 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.3333 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 418.32 | 2.49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 625 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 947.9166 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2475 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3895.8333 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160.7433 | 68.89 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 425 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10251.54 | 43.81 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.6667 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74 | 74 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 228 | 76 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 245.3332 | 230 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 344 | 86 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 840 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2187 | 135 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3093.375 | 109.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9760 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.5 | 11 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 205.3666 | 101 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1911 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.0113 | 2.53 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 514.1667 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5206.8333 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 253.33 | 72.38 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 562.52 | 80.36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 4535.44 | 142.4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.25 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.0667 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.75 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 294.8 | 88 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 726.6667 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1289.5832 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1620.3166 | 127.25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3397.1666 | 170 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.25 | 165 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.2333 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 134.6666 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162.5 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 232.65 | 33 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 260.7865 | 20.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 917.5833 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 977.4999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1330.4166 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1410.75 | 209 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.4925 | 69.99 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3175 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.655 | 26.1 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 407.5 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5552.3125 | 85.75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 996.6666 | 260 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1940.7333 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3195.9 | 201 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3433.3333 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7378.4166 | 185 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 329.9166 | 107 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 456 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1401.51 | 34.1 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1151.5665 | 193 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 622.8333 | 37 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 650-Fluidized Bed
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 11 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 15.4 | 42 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 714 | 42 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 860 | Co-generator Block | RFC | Off-Peak | 2693.3666 | 119 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 860-Co-generator Block
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 860 | Co-generator Block | RFC | Off-Peak | 833 | 119 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 860-Co-generator Block
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.6667 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.5166 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.9 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.2575 | 75.01 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 71.75 | 10.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82.7333 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 109.6666 | 329 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 119.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.2 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 191.1666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 209.45 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 259.6166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 293.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 311.9999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 460.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 505.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 513.1333 | 172 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 530.1 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 651.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 707.8458 | 34.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 752.8832 | 227 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 880.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 926.1333 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 951.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1193.8 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1658 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1705.8332 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2158.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3026.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4387.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5952.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9338.7499 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12072.8332 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.6333 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.5 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.3333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.6666 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.1333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.0333 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.55 | 13.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.4666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.3773 | 141.04 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.1666 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 123.6 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 131.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 151.0833 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210.5833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215.3333 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.5 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 252 | 252 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255.6667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 272.7666 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 282.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 540 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 560.45 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 584.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 660.3798 | 90.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 660.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 715.6665 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 813.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 815.4516 | 67.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 896 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1785 | 357 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2007.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2586.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2617.2 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2968.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4231.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4363.3333 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5094.25 | 287 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5775.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.9667 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27.7666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.0416 | 92.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57.3499 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 73.5533 | 23.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 107 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 111 | 111 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120.5 | 24.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 124 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 148.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 172.1999 | 184.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 173.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 226 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 252 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 266.6666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 374 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 525 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 573.1665 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 665.3833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 792 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 816.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1007.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1184.1663 | 490 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1813.7033 | 115.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1914.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3235.12 | 65.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4064.4998 | 330 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9026.8333 | 205 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 109.0832 | 385 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 311.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 66.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2074.6666 | 320 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 112 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 155 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 323 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83.6 | 41.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.1783 | 25.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 271.04 | 35.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1620 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13680 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19159.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1075 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3930.2 | 45.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5712.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 254.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 631.4666 | 148 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 951.6 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2584.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.6 | 54 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104.2333 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 124.3 | 113 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1259.65 | 61 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 68.85 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95.8332 | 230 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 115.7666 | 46 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 423.6332 | 358 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8.6666 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.8667 | 32 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 240 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3210.0332 | 158 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130.9499 | 81 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1276 | 120 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5858 | 58 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.1666 | 115 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 841.75 | 91 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 165.7166 | 163 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.9577 | 34.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.5 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.6175 | 20.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.6 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.8333 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97.5 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 99 | 198 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 127.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.2666 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 199.65 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 234.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 235 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 236.0333 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 338.9999 | 162.72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 339 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 364.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 407.3666 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 446.3499 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 532 | 380 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 541.6231 | 52.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 626.4 | 216 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 752.2166 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 801.8333 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1040.95 | 65.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1102.9 | 269 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1504.5 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1701.5999 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1848.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1926.4 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2794.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3005.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.0167 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.05 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.2166 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.8832 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.2 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.7 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89.04 | 95.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98.9966 | 87.35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.539 | 73.66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 139.4 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143.2432 | 175.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 145.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.8 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.4833 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188.4667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 301 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 333 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 343.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 392.7 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 397.8667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 467 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 691.2 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 750 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 878.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 879 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 991.9 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1023.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1052.42 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1116 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1168.1833 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1358.5388 | 90.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2102.6665 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5273.5 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9451.8665 | 247 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.2 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.25 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19 | 2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.1666 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.5 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 126.6667 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 133.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 222.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 323.4 | 154 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 523.5999 | 204 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 587.5 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 665 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 847 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 959.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 993.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1314 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1455.9999 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1540 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1652.1166 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1695.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2076 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2432.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11562.5 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 110.4166 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 216.1833 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 305.6333 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 88.8666 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 179.4 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 559 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.1233 | 24.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 843.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4070 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5100 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5734 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6528.06 | 127.17 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26367 | 187 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.7999 | 162 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 571.0833 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3902.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 236.8999 | 138 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3412.6333 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82.25 | 105 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 167.1166 | 37 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 834.9 | 66 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5217.3332 | 215 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 403.8666 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.1666 | 115 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195.25 | 55 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2829.2 | 132 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10727.1999 | 132 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 754.4495 | 466.67 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4059.9997 | 840 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 11.3333 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.7123 | 34.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.8 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.1318 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.5999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.5332 | 149 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 79 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 99 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.1 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 115.7333 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130.7333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 137.8667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 164 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.9167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.75 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 235.8499 | 159 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 260.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 269.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 291.4 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 305.0999 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 310 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 381.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 462 | 168 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 495 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 562.1 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 665 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 926.4 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1088.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1337.6 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1495.2 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2204.5833 | 71.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2254.4333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2841.6666 | 137.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4625.1 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11456.9333 | 232 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15802.5 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.8 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.0833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.8 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.8848 | 71.39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.7073 | 24.74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.5 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.6666 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.2 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.4166 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 106 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.5 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 139.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.21 | 125.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.35 | 171 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 168.21 | 62.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 262.5 | 50 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 316.2333 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 335.4666 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 370.1832 | 167 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 370.4167 | 25.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.65 | 11.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 417.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 437.5833 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 497.2 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 645.75 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 957.4666 | 172 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1288.8333 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1309.25 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1617.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1809.75 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2019.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2765.8667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4309.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4667.6665 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4.3267 | 23.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.5332 | 188 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.7833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.25 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.5266 | 62.29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.5 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.5333 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 73.5 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 76.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90.75 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.1333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135.6666 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 148.4332 | 146 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 166.5 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 176 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 183.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 220 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 267 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 314.5 | 370 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 341.2499 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 380 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 383.7999 | 228 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 404.8 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 410.9 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 509.95 | 217 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 575 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 579.5833 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 702 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 825.7499 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 857.01 | 95.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 895.35 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 969.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1245.87 | 65.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1246.3 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1282.55 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1496.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1560.88 | 65.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1605.4499 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3303.8332 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4807 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6120 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 279.0666 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 675.24 | 112.54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 731.4 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1852.9998 | 327 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4543.7665 | 503 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.2667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.8 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 203 | 40.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3309.3333 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 384.8 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 609.55 | 167 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.5 | 17.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 603.6333 | 91 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.9 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.86 | 16.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 676.2 | 48.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.82 | 24.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.9 | 26.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 557.6 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1270.3333 | 148 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12768 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30584.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.3166 | 49 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76.6667 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 231.65 | 113 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 279.7666 | 109 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1833.8666 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51.6 | 72 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 71.7833 | 73 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 171.15 | 163 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 117.9333 | 122 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 135.3 | 123 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 151.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 294.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 880 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 999.75 | 129 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.5 | 2 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 768 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2000 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6.6017 | 23.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.0333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.8675 | 183.47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55.8333 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 139.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 149.8 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 188.4 | 157 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 199.9999 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 210.6 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 211.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211.75 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 287.333 | 431 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 316 | 158 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 342.0533 | 25.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 354.25 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 357 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 469.3332 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 567.58 | 35.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 823.3333 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 841.75 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 911.821 | 34.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 929.45 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2202.9333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2480.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3023.6666 | 188 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3913.6666 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6323.3999 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9598.35 | 183 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.7333 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.1 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.8 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.865 | 46.95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.9126 | 45.16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.3333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.6667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.43 | 145.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66.5 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.5333 | 4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138.6666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 168.5833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 193.75 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 278.4 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 351.6 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 354.5833 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 368.5833 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 409.0666 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 437.4999 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 489.1 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 493 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 501.3332 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 668.8 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 919.6665 | 178 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1076.9517 | 47.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1115 | 223 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1166.5436 | 339.77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1334.6666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1426.1665 | 199 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1837.3333 | 208 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1860.7333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2656.8333 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5922 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5940 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16612.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.7 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 27.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.6833 | 133 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 42.5 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 87.7333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90 | 90 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 108.9 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 127 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 166.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 174.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 204.75 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 220 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 271.0667 | 15.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 418.5 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 496.6666 | 149 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 572 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 583 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 774.67 | 35.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 814.2 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 878.3667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1462.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1655.7499 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1996.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2091.7192 | 260.38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2455.6665 | 530 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7497 | 340 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 36.66 | 23.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.5 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 841.3999 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1541.9664 | 334 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 88.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 167.45 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 125.3333 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 184.5 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.1666 | 77 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 374.9566 | 114.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456.3 | 81 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 464.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 990 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1134 | 189 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9820.3333 | 68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14880 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.8 | 32.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135.2285 | 117.59 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 858.3033 | 68.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 127.125 | 28.25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 480.6666 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 546.25 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 704.9 | 133 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 57.6 | 36 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 74.75 | 39 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 96.0333 | 43 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 203.6667 | 47 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47 | 47 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 4027.3333 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.5125 | 56.41 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2953.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91 | 91 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 829.4 | 58 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2114.2666 | 101 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.8 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.0167 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.6 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.1 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.845 | 15.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.45 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.008 | 80.01 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.3666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.4 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.4666 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130.5 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136.3 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.3 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.5 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 285.2633 | 75.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 316.6667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 331 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336.4666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 386.75 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 426 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 432.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 489.8667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 525 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 529 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 625.4167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 655.2 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 695.02 | 36.58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1042.7833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1069.0666 | 152 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1145.8 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1159.2133 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1190.3367 | 34.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1594.4832 | 173 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2370.3332 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2371.4221 | 118.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2470 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4353.9166 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8624 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10129 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10870.9333 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.65 | 193 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.4666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.25 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.4167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.07 | 25.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63.9333 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.8 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.45 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.04 | 50.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137.5 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.3332 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 152.7333 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 167.2233 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 197.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228 | 11.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 293.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 410.0166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 416 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 474.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 714.6666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1015 | 350 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1030 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1084.9 | 14.25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1096 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1120 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1338.25 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9211.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12600 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.0667 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12.0133 | 13.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 78.2167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 120.5025 | 160.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150.3153 | 118.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 170.2 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 171.3833 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 275 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 302.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 333.3 | 202 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 345 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 557.65 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 901.45 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 943.4 | 356 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 978 | 163 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1001 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1219.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2662 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4243.7499 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28748.1333 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34273.8 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 200.01 | 66.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 202.5 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 269.01 | 89.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1850.7333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 166.5 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 320 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300.2766 | 105.98 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 359.6666 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2686 | 158 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8869 | 181 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.5717 | 22.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 315.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1320 | 110 | 1 | 4 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14700 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71 | 71 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.2 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 102.4 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 130 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 146.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159.1333 | 124 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 243.1 | 143 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 384.8 | 78 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1072.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1958 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.5 | 265 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95 | 57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 133.3332 | 250 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 165.75 | 195 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 302.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1729 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 126 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1721.4 | 114 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 53.9 | 66 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1999 | 156 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3588 | 780 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.2 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.25 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.3833 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.2 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 384 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 113.1666 | 194 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.8833 | 25.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 127.5833 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 148.75 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 151.6666 | 113.75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168 | 336 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210.7 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 240.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 261.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 301.93 | 65.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 320.07 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326.8333 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 418.0016 | 374.33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 562.8 | 402 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 684.5832 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 718.6666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 725.712 | 104.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 753.64 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 757.3331 | 320 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1001 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1101.75 | 195 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1256.2082 | 147.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2147 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2680 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3228.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4809 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6795.6666 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19381.4291 | 140.53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.2666 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.3833 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.6665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.5 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146 | 58.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168.5332 | 158 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192.5333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197 | 39.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 199.1833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 206.5833 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.3332 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.8 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 249.4166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 350 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 350.0233 | 85.72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 393.8332 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 656 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 791.1633 | 165.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 835.8333 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 849.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 925.65 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 978.9999 | 132 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1093.7166 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1671.2499 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2868.1166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3006.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.6 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.4 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.6 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 69.9867 | 18.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 71.43 | 23.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 74.4167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 92.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148.5 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 155 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 158.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.9166 | 85.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 196 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 200.5332 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 239.0333 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 246.6666 | 296 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 252.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 279.4333 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 444 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 486.9467 | 23.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 500.5 | 182 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 506 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 643.9 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 653.05 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 656.97 | 215.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 671.495 | 4.21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 798 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 934.5167 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2578.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6562.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36000 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120.05 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 254.4 | 159 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 91.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 97.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 176 | 96 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182 | 18.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 285 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 377 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1184 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1789.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123.2925 | 48.35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4966.3658 | 139.57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6212.4 | 186 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84.0666 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 125.0666 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 261.3 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.35 | 103 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 119 | 68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 828 | 184 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 71.0666 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8376.6666 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 79.3333 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120.9833 | 51.85 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 282.05 | 56.41 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 461.3166 | 89 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 648 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 44 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187.2 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 120.44 | 60.22 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 324.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1540.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 190.7666 | 59 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.2 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.6322 | 15.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.6166 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64.8083 | 111.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.6 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.7 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 89.7 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.6667 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.1667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150.15 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.56 | 140.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 208.4666 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297.25 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369.05 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 372.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 501.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 671.6666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 694.1333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 944.1925 | 38.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1890 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2057.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2135 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2298.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3411.2 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4189.65 | 90.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4735.8666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4987.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15178.2 | 61.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19066.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.25 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.0333 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.6 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80 | 20 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.3333 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.0833 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 153.45 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.8 | 2.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 167.1333 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 230 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 262.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 278.7 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 293.138 | 56.92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 317.8 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 397.4166 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 403.2 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 411.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 459 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 606 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 752.3333 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 834.1667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 907.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1182.5 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1671 | 557 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5095 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5145.8333 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5340 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 19.5357 | 11.38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.1166 | 131 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.8667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41.3666 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 59.45 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 102 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102.3 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108.5 | 310 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 109.9783 | 43.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 120.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 139 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 173 | 173 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 183.3333 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 197.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 229.9998 | 345 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 231 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 248.75 | 199 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 281.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 290 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 370.8333 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 383.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 388.31 | 75.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 407.0866 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 499.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 510 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 539.1 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 542.5 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 716.8333 | 34 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 726 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 824.1666 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1095.1999 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1142.32 | 65.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1180 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1458.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1904.3 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4920 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5903.9998 | 270 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6786 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9224.8 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14717.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 126 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 137.2666 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 157 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 279.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 427.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1094.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14117 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 538.9333 | 94 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2078.5216 | 109.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4893 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 428 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 720 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1505.8333 | 139 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14136 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.4999 | 105 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.3333 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 496.8 | 108 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8246.3333 | 220 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.8 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.7 | 43 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 98.6 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 177.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 292.6 | 84 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 370.5 | 190 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 111.1 | 22 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 167.6333 | 107 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 260.3499 | 123 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 896.1332 | 188 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 941.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 71.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1466.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8740 | 120 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 219.2 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 465.6166 | 91 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1264 | 120 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 258.5417 | 42.5 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2788.41 | 68.01 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3477.9166 | 85 | 1 | 1 | 0310-Pulverizer mills | U2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.8333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.7 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.4999 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.3333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.2267 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.6667 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.25 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.8 | 142 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154.9366 | 175.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 191.4 | 174 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 197.5125 | 52.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201.6 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 216 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 262.15 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 266.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 314.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 357 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 378.125 | 5.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 382.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 566.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 661.2666 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 682.2666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 816 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 862.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1078.01 | 65.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1094.4 | 288 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3521.375 | 71.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3839.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4440 | 222 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13863.9333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22409.55 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.8333 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.3329 | 680 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.6667 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.12 | 50.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.7333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.7333 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.7426 | 49.01 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.6 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74.1 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.97 | 165.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.2 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.9599 | 155.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.25 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.7 | 7.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.0573 | 59.72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 237.6 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 265.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 295.2333 | 2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 308.72 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 311.15 | 25.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 336 | 168 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 368.9073 | 66.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 439.9 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 556.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1513.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2361.7 | 49.72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15867 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.1818 | 6.89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 98 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 142.2666 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 194.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 196.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 199.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 223 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.8666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 227 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 234.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 262.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 283.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 345 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 372.75 | 213 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 491.8333 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 515 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 540.8 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 544.5 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 624 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 642.5666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 690 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 734.66 | 65.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 741.8666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 918.3333 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 989.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1062.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1272.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1280.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1688.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1900 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1935 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2101.3332 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2793.6 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2978.4997 | 483 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3089.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4400 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7238.3332 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71.05 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 364 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1623.5998 | 297 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11782.05 | 687 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3292.0666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.95 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 96.9 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1350.1 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.28 | 55.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 394.1999 | 81 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1430 | 130 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2675.4 | 63.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.315 | 23.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 245.6667 | 22 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 208 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 679.05 | 27 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23 | 12 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 102 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 142.9333 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 296.4499 | 147 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 438.1333 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1061.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2152.9332 | 134 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2826.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4399.3 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.8 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 109.9998 | 300 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 152.75 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 163.0333 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 232.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.65 | 39 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 363 | 121 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3555 | 20 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 79.2 | 88 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2419.6664 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1603.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | U2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 61.6 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 353.8 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 94.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 522 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1076.3666 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 188 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1982.6331 | 293 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 344.4999 | 318 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 422.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1237.5 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 988.9 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 4.8333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 818.1333 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1642.1666 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 16.5 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 664.7331 | 338 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 97.5 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 319 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 246.5 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 39.5 | 158 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 285 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8606.6666 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10766.9999 | 180 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 104.6332 | 146 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 472.3333 | 109 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 292.3 | 44.4 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 411.95 | 77 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1084.45 | 69 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2301.6666 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5161.2 | 184 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.7333 | 112 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.5 | 6 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.2167 | 29 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146.2 | 34 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 438.9 | 77 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8740 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22550.4997 | 510 | 1 | 1 | 0312-Pulverizer mill classifiers | U2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.8 | 174 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 849.6999 | 174 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2231.6666 | 260 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 48.9333 | 73.4 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.5 | 30 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 245.7666 | 146 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1242.0833 | 55 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2878.2 | 117 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 544 | 80 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 936 | 72 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123.75 | 75 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.6666 | 95 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245.3333 | 64 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.6333 | 122 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2028.1664 | 430 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94 | 94 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 312.4166 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6727.5 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1986.5 | 145 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 564.4266 | 55.7 | 1 | 1 | 0312-Pulverizer mill classifiers | D3-Forced - Postponed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.5 | 5 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1170 | 130 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.8333 | 26 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 616.25 | 85 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 506 | 92 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3182.4 | 102 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3660.05 | 71 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 282 | 24 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 416 | 52 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 289.3333 | 80 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 845 | 130 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.3333 | 80 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48 | 80 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 283.5833 | 5 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 288.5499 | 87 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0314 | Pulverizer mill ball charger hopper (ball mills only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1219.3332 | 155 | 1 | 1 | 0314-Pulverizer mill ball charger hopper (ball mills only) | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 102.641 | 71.61 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224.28 | 26.7 | 1 | 1 | 0315-Pulverizer mill coal level controls | D2-Forced - Delayed | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109.25 | 95 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 708.3332 | 170 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 214.5 | 66 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.5 | 15 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1026.6 | 116 | 1 | 1 | 0315-Pulverizer mill coal level controls | U1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360 | 60 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65 | 78 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92 | 80 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 378 | 140 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1002.7 | 111 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42 | 42 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 99.9 | 37 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285.9999 | 165 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 589.9 | 102 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 810 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1536.2999 | 162 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.6667 | 16 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.6666 | 58 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63.9333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1708.1833 | 113 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.6 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 106.7093 | 50.02 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 284.8499 | 81 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 384.8083 | 75.7 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.8333 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.3333 | 92 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285.5833 | 115 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 930.4166 | 145 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 943.6665 | 190 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 21 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.25 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91 | 14 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 294 | 72 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 401.4 | 54 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 596.2666 | 52 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 17.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135 | 45 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 744 | 80 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.9333 | 13.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 454.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7914.8 | 842 | 1 | 1 | 0320-Foreign object in Pulverizers mill | U1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.5 | 21 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.9333 | 112 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 695.7499 | 165 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 971.7499 | 195 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 107.6913 | 48.22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266.5 | 65 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 365.5833 | 205 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.2567 | 20.2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.1667 | 1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 396.75 | 115 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.8 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.6666 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.25 | 67.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.4 | 72 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 678.1666 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5648.4999 | 165 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1271.5426 | 139.22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 974.61 | 139.23 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 235.95 | 39 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 357.75 | 53 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.3333 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 305.25 | 165 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 315 | 84 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 331.1037 | 24.74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 680 | 170 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 418.1 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2320.2 | 108 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 41.0387 | 43.97 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.5 | 65 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 119 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 864 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 928.5833 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9422.5833 | 145 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.8833 | 31 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.75 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 320 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2425.3 | 158 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.05 | 107 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 41.9253 | 22.46 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 428.8 | 128 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1141.25 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1794.5999 | 108 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 400 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.42 | 15.9 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.335 | 27.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21.2 | 24 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 216.3333 | 118 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 240 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.6 | 48 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.7666 | 122 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.25 | 115 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3300 | 165 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.4666 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.05 | 51 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.15 | 15.9 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.72 | 29.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.66 | 22.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.25 | 71.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.4 | 16 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 574.875 | 109.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 869 | 44 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6655.4999 | 162 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.5 | 110 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.2 | 36 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138.7 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.25 | 75 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42.8999 | 234 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 62.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 85.8666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.4 | 48 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 304.3333 | 110 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437.4 | 108 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.564 | 56.41 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 291.0666 | 118 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1262.9333 | 148 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 822.25 | 55 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 376 | 94 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6908.0833 | 95 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.6666 | 155 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.6667 | 10 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1059 | 60 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.5333 | 23 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.3333 | 80 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 671.15 | 31 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3153.75 | 75 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 256.6666 | 100 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 353.3333 | 50 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26 | 30 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 638.1666 | 70 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.0833 | 35 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 146.7433 | 33.1 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.0833 | 73 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 666.5 | 155 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 699.6 | 88 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 775.2 | 38 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 928.6666 | 140 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2202.2665 | 199 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2963.0666 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.7166 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.2 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 431.1666 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 808.8333 | 211 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1572.2666 | 134 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.6667 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 189.5833 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 939.0985 | 39.99 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1001 | 132 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | U1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 469 | 42 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 865.3332 | 295 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1171.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2682.1667 | 38 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2697 | 174 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.625 | 147.5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 157.0833 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287.5 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 870 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.2 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 699 | 139.8 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.5 | 62 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 111 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 100.45 | 41 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437.8999 | 174 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.6 | 28 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 468.7666 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1122.9166 | 77 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.1 | 66 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.0667 | 32 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 246.7166 | 113 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.7333 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.8 | 46 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 130.8333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.25 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.8333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 164.25 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 959.8999 | 174 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1908 | 72 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.5 | 46 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92 | 46 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 183.6 | 34 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 338.3333 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1458.5666 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.5 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 282.75 | 195 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1504.9999 | 210 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.75 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 185.6 | 128 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 284.1666 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.25 | 63 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 302.25 | 195 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1437.3333 | 154 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2636.1 | 174 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.6667 | 2 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 14 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 381.4166 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1283.25 | 177 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.6316 | 91.94 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 108.1 | 46 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.52 | 18.4 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 323.4333 | 62 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.9 | 31 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.4167 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 191.2166 | 77 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195.2499 | 165 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 654.9 | 177 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 995 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 252 | 36 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.5 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 343.65 | 87 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120.5333 | 64 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 121.55 | 51 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 183.9333 | 62 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 124.8833 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 236.4 | 72 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.5 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.15 | 269 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 104.5 | 38 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278.1 | 81 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.3333 | 8 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.5 | 18 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.9166 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.1466 | 62.3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200.4666 | 124 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225.3333 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238.3333 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 389 | 97.25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 485.0666 | 68 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2306.3332 | 340 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.85 | 127 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 203.55 | 69 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.9166 | 43 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 284.9 | 66 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 856.3333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297.0833 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 367.2 | 68 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.32 | 15.2 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 143 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 248.5 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 219 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.3333 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 434.8667 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 476.6667 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1216.6666 | 125 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7579 | 143 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1458.3666 | 134 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.5 | 33 | 2 | 2 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 440 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2344.9166 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.6666 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 70 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 178.8333 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 567.6666 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1812.4999 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 291.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 457.2 | 127 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3386.4999 | 195 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 124.6666 | 68 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 440.2999 | 111 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1072.5 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 228 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 386.6666 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 823.3499 | 99 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1653.3332 | 155 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 172.0666 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.6 | 72 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 133 | 84 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 145 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 408.25 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.35 | 63 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 87.2 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1091.6266 | 96.32 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39642.0566 | 58.3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14171.3331 | 580 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | U1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3333 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.3333 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.2917 | 24.5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 245.7333 | 19 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 412 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450.4165 | 235 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1406.6666 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3702.2499 | 177 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 94.6666 | 71 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164.3333 | 58 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460.1333 | 119 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2040 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 262.5 | 210 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 564 | 94 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 822 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.3333 | 35 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 274 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 393.6333 | 98 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.25 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.6666 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.6 | 72 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 92.5 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211.25 | 169 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 289.5999 | 96 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.8333 | 11 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 176 | 66 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 285.9999 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 540 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 878.5 | 35 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 422.4166 | 137 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 680 | 85 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 270 | 180 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 483.75 | 135 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 142.4833 | 83 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 12 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.2 | 42 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.0167 | 47 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2781 | 81 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 328 | 24 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 444.3333 | 86 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1026.6666 | 110 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1914.6666 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.6667 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66 | 12 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.25 | 11 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 221.9999 | 180 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17079.6 | 331 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6704.1 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.4333 | 19 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 121.7166 | 109 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204.1667 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 274.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2031.0333 | 43 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 342.2666 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474.03 | 62.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1513 | 178 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.66666 | 4 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.3333 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 470.6666 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 696 | 240 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1477.2333 | 91 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 50.3999 | 189 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 158.3333 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48.9999 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 171 | 57 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 72 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84.1166 | 49 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 149.4 | 108 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 267.2 | 96 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 425 | 170 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 886.5333 | 109 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134.9883 | 19.9 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 209.0833 | 193 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 275 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 473.3333 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7035.45 | 93 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 383.8333 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 492 | 4 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 521.0375 | 142.75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 782 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.25 | 27 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 527.8 | 91 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 260.4 | 124 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 164.8 | 48 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1940.6665 | 410 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2221.45 | 577 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91.6667 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.3333 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 256.6666 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2652.6666 | 92 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6500 | 250 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.75 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66.6666 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 429 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 702 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1453.3333 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437.5 | 125 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 734.6666 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2034.3332 | 340 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 145.3666 | 49 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112 | 48 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 173.8666 | 64 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 263.3333 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 575 | 230 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1014.6666 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 153 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 306 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 454.1833 | 119 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 733.3333 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 939.12 | 50.31 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2337.25 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33.9166 | 37 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 696.6665 | 190 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115.3066 | 108.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 699.6 | 106 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 248.4166 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 389.25 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 712.0166 | 119 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 837.2 | 161 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 153 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 493.35 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 646 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 981.3333 | 184 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.25 | 5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.775 | 26.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1599.75 | 81 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 490 | 98 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205.8333 | 130 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 44.1667 | 5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 41.3 | 118 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51.5666 | 119 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74.2499 | 405 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 125 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 513.3332 | 140 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 974.4666 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1075.4166 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1.0833 | 13 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.5833 | 43 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.1666 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.9167 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.9166 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.9666 | 169 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 152.1666 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.8666 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 867.9999 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1137.5 | 182 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1816.1666 | 170 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.1666 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1285.9832 | 131 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 293.2166 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2368.8 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 641.6665 | 220 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 328.6666 | 170 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 455.2166 | 143 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 450.1166 | 239 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1534.5829 | 635 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.35 | 83 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 420.75 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 433.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 817.9999 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1193.75 | 125 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.75 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.9999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99 | 33 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 292.1333 | 28 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 310.5 | 207 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 312 | 160 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1023.75 | 195 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 23.078 | 41.96 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.7666 | 107 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 110.9928 | 48.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 156.2166 | 103 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 168.75 | 67.5 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 237.6 | 66 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 324.85 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 579.2691 | 48.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 610.038 | 38.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 664.5833 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 822.25 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1034 | 220 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.7 | 37.4 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 201.3 | 66 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 455 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2808 | 135 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.0167 | 13 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.75 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 99.6666 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 247.9166 | 125 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262.4666 | 62 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 440.2 | 93 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 741.9166 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.7833 | 103 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 192.99 | 64.33 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 247.5 | 198 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 751.3333 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2.6666 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.8333 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42.6666 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 77.2525 | 71.31 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 83.6 | 44 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125.4 | 66 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 282.7999 | 303 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 289 | 102 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 728.3398 | 48.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1039.6 | 138 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 878.7999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 902 | 220 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 111.9333 | 46 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.4333 | 71 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6725.2 | 172 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.4167 | 13 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.25 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 549.5999 | 144 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1116.35 | 269 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3544.1 | 83 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.6 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.75 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.6666 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.1667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 224 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 297.6 | 96 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 362.4333 | 83 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 399.5 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 537.6 | 144 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.2 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.5 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.6999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 29.166 | 48.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 157.9999 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 177.65 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 236.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 367.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8867.4999 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 353.0666 | 132.4 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1092.5 | 190 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131.3999 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 835.625 | 143.25 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.6667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.6665 | 220 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 476.0833 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 347.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.65 | 9 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.1667 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.746 | 34.67 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 251.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 601.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.75 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 26.0333 | 71 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.8 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 153.75 | 123 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 600 | 96 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1015.92 | 199.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5.5 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10.9395 | 38.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 47.9563 | 49.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.75 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 225.2263 | 48.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 237.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 389.8082 | 161.3 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.4666 | 83 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 709.3331 | 320 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.7833 | 101 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 164.3333 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39.1 | 34 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 461.25 | 123 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 969.9999 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2479.9999 | 75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3503.3332 | 200 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.0833 | 19 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.5 | 9 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.2 | 13 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59.96 | 59.96 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.2666 | 89 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 490 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1242 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 182.1503 | 28.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198.95 | 69 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 670.0833 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 922.2 | 63.6 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2310.7998 | 318 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.6667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1890 | 140 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 173.7783 | 82.1 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198 | 36 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 208 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1065.1666 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1123.2 | 192 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.9167 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.5 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 256 | 160 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 543.2499 | 123 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1685.6 | 28 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2812 | 148 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5270.4998 | 249 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.4 | 36 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 28.525 | 57.05 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 39.1235 | 60.19 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 44.3522 | 50.21 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 147 | 42 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 237.3788 | 48.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 860.8333 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1458.3333 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1876 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 165.9 | 63 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 597.5249 | 231.3 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.9999 | 180 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 490.9333 | 56 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.3333 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1418.25 | 93 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3121.0831 | 335 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276.5 | 79 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.9999 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 728.3332 | 230 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1159.3333 | 74 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.9 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32.6667 | 14 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.2 | 194 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 227.65 | 157 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 242.8333 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4642.0833 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10624.1666 | 122 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12 | 48 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 25.1151 | 48.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.9999 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 123.228 | 44.01 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 204.7333 | 37 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 291.5949 | 120.66 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 555.3333 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 570.4 | 124 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 264.3333 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.4 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1494 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2486.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.9999 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 207.7 | 93 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 48.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 650-Fluidized Bed
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 530 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.05 | 7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.6666 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 331.8666 | 152 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.8333 | 5 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.1667 | 14 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51 | 17 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.8665 | 199 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123.2 | 96 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 286.245 | 63.61 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1274 | 49 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3978.3333 | 220 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 105 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302.4 | 96 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17 | 170 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.9333 | 88 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 371.6667 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 113.75 | 175 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 115.5516 | 72.98 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 383.5999 | 84 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D3-Forced - Postponed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1530 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D3-Forced - Postponed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 969.15 | 117 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234 | 234 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 456.6333 | 103 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6398.5 | 67 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.6666 | 31 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1423.9999 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 79.9999 | 75 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 424.6666 | 98 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2455.65 | 459 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1062 | 118 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1658.7 | 342 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.4333 | 7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.1667 | 10 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.7333 | 92 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 109.3333 | 82 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.8333 | 166 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 201.25 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 420 | 35 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 228.0833 | 119 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 346.2665 | 392 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 308 | 105 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 900 | 60 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 9 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.3333 | 46 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 642 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81 | 27 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 195 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276 | 8 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 385.4167 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1312 | 32 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 87.75 | 117 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 94.49 | 85.9 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 385 | 77 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 821.2417 | 34.1 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.8333 | 145 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196 | 98 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1028.5 | 22 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2372.5 | 65 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66 | 8 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 152 | 38 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203 | 29 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 402 | 67 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130 | 60 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 307.4166 | 85 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.5833 | 235 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 223.5998 | 258 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2 | 6 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.6166 | 77 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 295.75 | 91 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 768.1999 | 138 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1850.3333 | 244 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.75 | 191 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.8 | 48 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121.2498 | 291 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 159.75 | 45 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 550 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 641.6665 | 250 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 885 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1900 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.6667 | 50 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.6666 | 52 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 259.1749 | 88.86 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 382.3333 | 114.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74.3333 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224.4666 | 52 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190.3 | 22 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.3333 | 46 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.3333 | 85 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.75 | 103 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 280 | 80 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 162.9166 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.4 | 108 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.4 | 4 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 450.8333 | 25 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 78.1207 | 20.74 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.1 | 18 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.7 | 14 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39 | 78 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84.2333 | 38 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 115.2 | 128 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 805.5 | 54 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2742.6761 | 46.87 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 478.16 | 59.77 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.4667 | 8 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20529.3787 | 261.91 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 325.7999 | 108 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24626.1 | 498 | 1 | 1 | 0339-Pulverizer System Puff | SF-Startup Failure | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3397.5 | 30 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 184.9333 | 38 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 189.8 | 78 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 690.71 | 34.68 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1823.67 | 88.1 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.3667 | 38 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.2666 | 53 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 618.3333 | 53 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 541.3275 | 103.11 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 849.1047 | 23.63 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5199.612 | 35.81 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3334.6665 | 410 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 129.9999 | 78 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 289.8 | 28 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 111 | 36 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 498.7496 | 35.71 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 702.31 | 35.56 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184 | 46 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48.6666 | 73 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 155.1667 | 38 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 390.1617 | 13.1 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2 | 2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.8332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.6666 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 70.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.6666 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.0666 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.1 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 162.9166 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 199.5 | 114 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 200 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 288.0916 | 95.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 288.75 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 339.2 | 106 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 406 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 455 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 461.9333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 612 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 677.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 786.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1006.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1323.1666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3780.8748 | 304.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4050 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5964 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11970.8333 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13704 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.25 | 3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.1666 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.69 | 22.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.1833 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 133 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 289 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 302.4 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320.8333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 327.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 378 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 425 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 459.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 465.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 480 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 531 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 560 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 587.4166 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1114.6665 | 190 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1550 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1629.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2300.36 | 39.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9153.65 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.9166 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.4 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 87 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125.5832 | 137 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 149.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 176.7 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 187 | 187 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 216.4166 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 223.8665 | 184 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 241.6666 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 617.4166 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1932.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2037.2 | 132 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2093 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2813.3333 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2844.1667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9477 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.5015 | 56.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 54.1666 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 113.7499 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 627.45 | 418.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 113.75 | 113.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141.3333 | 53 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 632 | 79 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 341.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160 | 120 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 519.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4048.25 | 15 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2290.4167 | 5 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14474.6666 | 320 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.8333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93.4375 | 81.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96.9 | 114 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104.3666 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.75 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.0188 | 52.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.8332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 219.8666 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 226.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 250.25 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 319.5833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 342.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 384.1833 | 89 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 420.9666 | 146 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 452.3333 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 931.2916 | 271.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 977.0833 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1568 | 320 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2600 | 81.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3611.6165 | 211 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4142.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4759.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.75 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.0999 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.0833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.9832 | 173 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 149.3332 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215.3333 | 76 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 215.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 288.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 309.0666 | 152 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 431.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 591.0666 | 104 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 777.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 881.4 | 113 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 882 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1115.1 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1712.825 | 39.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2015.55 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3366.5333 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.5 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.1666 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.24 | 23.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.3793 | 118.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89.0664 | 334 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.24 | 79.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 155.7999 | 114 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 264 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 308 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 366.6 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 408 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 439 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 477.85 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 837.1 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 968.5832 | 197 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1243.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1386 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1836.55 | 69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2042.8332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3570.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12320 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.3925 | 91.19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 91.7092 | 393.04 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 315.16 | 78.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 731.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17426.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 128.46 | 42.82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 337.98 | 56.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 357 | 89.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 489.99 | 163.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118 | 59 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 424.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174 | 87 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 405.3331 | 320 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2.5833 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.0455 | 57.51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 143 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 261.45 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 337.625 | 109.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 387.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 497.0333 | 114.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 595.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 719.6874 | 176.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 813.3331 | 305 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 831.25 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1065.9999 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1957.9999 | 165 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2571.5625 | 81.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6520 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12829.7 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.5 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.7 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.4 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 159.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 179.0833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 214.7 | 114 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 251.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 307.0833 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 360.7624 | 99.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 367.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 485.9333 | 148 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 490.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 808.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1302.1 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1828.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3574.5666 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3931.2499 | 375 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5735.38 | 57.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.41665 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.75 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.0733 | 62.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.2 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.45 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.45 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.225 | 61.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.7 | 9.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.0905 | 134.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71.295 | 29.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.46 | 42.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 122.4664 | 334 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148.5 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 150.15 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 172.25 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 279.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 588.75 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 633 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 762.6833 | 67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 796.0332 | 143 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 933.3 | 183 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 992 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1108.3332 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1678.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2535.2 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3123.2 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18336 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20580.8333 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.9709 | 82.89 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 130 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 152.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 361 | 72.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1385 | 346.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 234 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 263 | 65.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 658.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 605 | 110 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 302.9999 | 180 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30643.2 | 228 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1052.6333 | 23 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.65 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.65 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.0167 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.6667 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 108.0625 | 61.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 185.3 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 198 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 202.6665 | 304 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246.884 | 39.82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 313.3333 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 417.0833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 448.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 700.7 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 818.2083 | 91.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 851.9833 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 970.3332 | 164 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1160.6166 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1232.5 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1502.9166 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1629.3333 | 104 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1830.4333 | 178 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3148.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3294.6875 | 81.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3399 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5041.6666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6495.5833 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7097.5 | 283.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7920 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.80166 | 3.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.4667 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.08 | 39.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103.8 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 152.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224.5833 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 232.56 | 61.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 243.7499 | 225 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 442.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 670.7 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 843.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 847.8586 | 137.12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1006.5 | 165 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1044.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1203 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1331 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1606.5 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1636.8 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2493.505 | 37.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.0167 | 9.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.5333 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100.8333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 128.75 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 208.1593 | 183.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 222 | 148 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 248 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 258.3999 | 114 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 301.4666 | 66.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 318.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 338.4 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 362 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 516.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 547.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 572 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 633.75 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 715 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 761.2499 | 157.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1005 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1296.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2710.25 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3135 | 285 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3597.4999 | 150 | 1 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 178.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 466 | 69.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2407.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 173.24 | 86.62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 639.78 | 106.63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 839.99 | 88.42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1132.3998 | 228 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 333.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 858.3333 | 103 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1458.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1401.6757 | 188.99 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 682.9931 | 80.51 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1329.4 | 138 | 1 | 1 | 0340-Other pulverizer problems | SF-Startup Failure | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 38.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.4166 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81.0666 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.9791 | 81.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.75 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148.75 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 155.55 | 54.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 225.4266 | 42.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 260.2665 | 244 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 515.6666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 568 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 620 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1707.6666 | 109 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1750.3333 | 118 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3611.5 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14158.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.5333 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.045 | 71.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.75 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.6 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.0833 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 189.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 307.5 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 346.6666 | 260 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 366.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 594 | 198 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 924.5 | 215 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1540 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3117.8333 | 130 | 1 | 3 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10059.7499 | 135 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12353.3333 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16343.9833 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 47.5999 | 204 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 55 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.35 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.9167 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.8 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 118.25 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 153 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 260.4167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 345.1 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 408 | 204 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 428.75 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 514.2799 | 167.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 514.8 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 660 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 803.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 828 | 69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 892.9998 | 228 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 908.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 999.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1285 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2106.0333 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4676.25 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9399.75 | 249 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.07 | 72.07 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 787.525 | 92.65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 829.9703 | 74.66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1316 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 227.61 | 75.87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 616 | 32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 160.702 | 84.58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 167 | 41.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 215 | 53.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 279 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 557 | 278.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 597.3033 | 96.86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 338.8167 | 29 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1059.1 | 62.3 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1087.5 | 87 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.9 | 113 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1284.3998 | 507 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1311.3166 | 101 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 42.25 | 169 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.1666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84.8666 | 76 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 114.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.375 | 7.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 167.9999 | 288 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 187.5 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190.9333 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 191.25 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 260 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270.6666 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 373.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 385.4166 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 491.75 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 507 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 658 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 679 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 747.5 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 767 | 118 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 868 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1122.9 | 394 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1134.6 | 244 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1300.5 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1313.5416 | 81.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1320 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1393.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1649 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2184 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2351.4166 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2928.99 | 109.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3338.4912 | 225.32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4155.9633 | 114.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4488.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7535.4167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8194.9375 | 128.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22899.8666 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.5 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.9999 | 252 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118 | 118 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137.6 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 181.8 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189.5833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 212.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 213.0375 | 109.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 330 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 342.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 438 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 454.6666 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 520 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 555 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 567.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 814 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 923.7833 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 945 | 135 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1027.5833 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1334.9999 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1618.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3263.5883 | 121.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4679.1 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.1333 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94.6 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 119 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 120.5999 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123 | 123 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 172.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 186 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 197.1999 | 204 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 201.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 202.6666 | 152 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220.8333 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 316.8 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 320 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 348.5 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 368.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 518.4 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 537.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 979.8 | 3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1167.75 | 135 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1804 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2283.3332 | 137 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3948.75 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 555.9 | 111.18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1320 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 183.99 | 61.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 348.48 | 87.12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 116.92 | 58.46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 161.01 | 53.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 413.7 | 68.95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 71.8667 | 14 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1095 | 300 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8540.2916 | 62.3 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 60 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 290 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2925 | 25 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5160 | 600 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.5 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.0833 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78.4 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 87.4666 | 164 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.7333 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225.4665 | 178 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 250.0666 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.4999 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 344 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 405.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 434 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 459.9 | 146 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 487.4999 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 742.6 | 158 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 759.5 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 838.95 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1129.3333 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1395 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2376.6666 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2440.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3584.9999 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5213.375 | 223.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6354.9833 | 64.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9697.4998 | 270 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10159.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.5 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.75 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.4999 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 292.5216 | 58.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 318.7499 | 76.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 366.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 464 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 526.5 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 611.3332 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 634.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 697.495 | 59.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 950.8333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1069.5833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1211.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1395 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.64 | 16.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.9166 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.7467 | 19.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.9 | 67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102.0833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 115.8666 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 137.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 152.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 298.4666 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 357 | 204 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 437.6667 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 610 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 615.6 | 114 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 618.7832 | 137 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 762.415 | 109.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 950 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1005.5833 | 109.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2620.895 | 114.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 26.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.9983 | 77.14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 91.884 | 88.92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 546.03 | 60.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 503.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1455.3999 | 114 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 288.7499 | 157.5 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.3333 | 160 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13123.8 | 634 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19069.9998 | 600 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1942.5663 | 577 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17.5 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.145 | 18.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 59.5 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 86.25 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.75 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 122.6709 | 120.66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.8 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 257.5 | 103 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 348.5 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 366 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 577.9166 | 91.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 635.1041 | 81.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1694 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1759.6 | 424 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1963.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3686.4 | 38.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5062.8332 | 370 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64590.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.6333 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60.6666 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79.2667 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.2666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 132 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 159.3833 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 176 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 184.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 257.1332 | 275.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 277.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 285 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 541.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 617.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 695 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1045.9333 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1116 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1289.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1348.5 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1635.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1733.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2339.3333 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2432.055 | 57.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2558.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14182.6833 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.25 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.75 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.5 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.25 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 117.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 120.4 | 84 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 174.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 197.4266 | 53.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.6667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 251.5999 | 204 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 284.9166 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 322.8 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 334 | 167 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 558.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 625.4166 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 819.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 888 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 888 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 909.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1127 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1994 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2114.5832 | 203 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75.67 | 75.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 422.725 | 68.55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 895.32 | 223.83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1399.97 | 107.69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 297.4891 | 87.07 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49 | 24.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 168.99 | 56.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 616.7 | 123.34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 634.4266 | 64.3 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2371.7 | 128.2 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2384.6666 | 73 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138.45 | 117 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 29.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 21.5 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 496.6667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 788.3333 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 4768 | 298 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 681.4667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1460.8666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 127.5 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 702 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 929.3332 | 328 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 310.3 | 58 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 124.7 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1815 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3218 | 40 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.8333 | 70 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2660 | 70 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1958.3333 | 100 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 554.9999 | 90 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 991.25 | 65 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 443.3333 | 70 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 275.6432 | 127.22 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 480 | 75 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1076.25 | 105 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 175 | 140 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.1666 | 34 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 237.795 | 57.3 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 585 | 195 | 1 | 1 | 0342-Pulverizer inert system | D3-Forced - Postponed | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.2933 | 138.4 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 870.4 | 108.8 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.3333 | 98 | 1 | 1 | 0342-Pulverizer inert system | D2-Forced - Delayed | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 450 | 225 | 1 | 1 | 0342-Pulverizer inert system | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.5333 | 8 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.6 | 19 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63 | 14 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 243.9998 | 240 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 457.1666 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 478.75 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 643.5333 | 98 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 750 | 75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14693.3333 | 64 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.2 | 21 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.48 | 39.08 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8643.2 | 64 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 996.6666 | 200 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4230 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1271 | 60 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 946.3333 | 85 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6146.6 | 146 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2736.2833 | 73 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.5667 | 29 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30.3333 | 28 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71.5 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 345.3333 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 398 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1245.8332 | 250 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1948.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2042.9999 | 108 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2460.3333 | 220 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.75 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.25 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.75 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 208.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 214.3333 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.0517 | 4.42 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 765.0375 | 79.83 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1404 | 108 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1194.75 | 81 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3658.5832 | 215 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1356 | 113 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 98 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 294.6666 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 355 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 658.3333 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 712.5 | 38 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9551.8999 | 138 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3035.9333 | 124 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.8 | 78.8 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3143.8666 | 68 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5922.3666 | 79 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6475.3 | 102 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19620.4333 | 58 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 970.8 | 72 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.1833 | 23 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68.9 | 53 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 115.0333 | 14 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 249.1333 | 74 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 711.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 137.7 | 27 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174.4 | 24 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 438.0833 | 35 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1135.7 | 138.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2158.3333 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45 | 135 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 119 | 17 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1020 | 85 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105 | 100 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 333 | 111 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 519.9166 | 85 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2292.8666 | 163 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2662.8 | 63 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.8333 | 5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61.6666 | 25 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130.3332 | 230 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302.5 | 55 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 304.8 | 20.32 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1645.3333 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.0333 | 103 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.6 | 46 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 788.9999 | 180 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7066 | 120 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.1708 | 70.01 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 490.8333 | 190 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 246.7166 | 131 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 709.883 | 120.66 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4100.8333 | 133 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7334.1666 | 65 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.2 | 18 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 168.2 | 58 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 253.15 | 61 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 371.3333 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 452.4 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1875 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2145.7333 | 121 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161.9167 | 14.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240.461 | 20.67 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 429.2833 | 43 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7082.1666 | 110 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 800 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 594.48 | 74.31 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1171.0833 | 115 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 855.5333 | 82 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9253.9 | 58 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204 | 34 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 238.25 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 504 | 42 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 509.8333 | 35 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 851.9999 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 542.05 | 111 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 666.5 | 43 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.7333 | 8 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105.3 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 444.5 | 70 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 621 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 937.5 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3187.2 | 64 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16807.5 | 83 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.5 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.5833 | 14.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 206 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 595.4666 | 58 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.0666 | 46 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 850.2 | 52 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1711.9666 | 161 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.3333 | 116 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7743.1333 | 38 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7800.7333 | 68 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 221.6666 | 70 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 573 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 660.1 | 24.6 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14050 | 120 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 110.4 | 4.8 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 683.1 | 6.9 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 188.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 634 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5239.3333 | 58 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 450 | 75 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.5667 | 38 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 219 | 90 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 575.6133 | 18.4 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2787.6 | 20.2 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.8 | 76.8 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7847.76 | 14.4 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1762.3333 | 68 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19274.4333 | 73 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 537.3666 | 137.2 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 842.4 | 108 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15482.5833 | 59 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1035.0666 | 56 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6472 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.5 | 150 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 320 | 80 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 438.8666 | 58 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12837.3 | 42 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2094 | 120 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22692 | 60 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 95.3333 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6257.2333 | 58 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2038.5733 | 15.2 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.1 | 54 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2698 | 38 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.3333 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43 | 60 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 751.6667 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12836 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20280 | 65 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.44 | 14.4 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.2 | 2.8 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 495 | 108 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 589.1667 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1322.4 | 48 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3290 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10495 | 100 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 691.8167 | 13 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2406.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.6041 | 28.75 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 338.4 | 108 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 480 | 120 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 356.25 | 25 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 663 | 13 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140.875 | 28.75 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.9 | 7.1 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6297.4 | 23 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2394.6667 | 32 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1347 | 18 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.9167 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.3332 | 131 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1093.3333 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 187.7665 | 262 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 213 | 142 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 485.3333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14.1333 | 16 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.6666 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.2 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.3333 | 190 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.3166 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 311.0333 | 86 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 146.6665 | 220 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 158.5666 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 186.2 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 310.8 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 593.75 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171.1333 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1096.2 | 116 | 1 | 1 | 0346-Pulverizer pyrite removal system | U1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.05 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 244.95 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 378 | 72 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.4703 | 47.57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 569.3332 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 805 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2438.9333 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1899.4999 | 174 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.25 | 105 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.1666 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 70.2666 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.1666 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 128.6498 | 249 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 256.5666 | 86 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 354 | 72 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.5333 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.6 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 71.8666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 165 | 66 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 415.4999 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 88.1666 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 169.5833 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1423.75 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 430.7375 | 60.81 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.5 | 15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.9333 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 12 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 405.9999 | 105 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1740.48 | 155.4 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3348.3332 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2207.9165 | 175 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 71.3333 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 364.5 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 466.9333 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1721.75 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.5333 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.0833 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.9667 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.4 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.7 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 114.2333 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.5 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 273 | 130 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 356.4 | 132 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 103.1333 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.8 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 265.8333 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30.3333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.2 | 72 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95.5832 | 155 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 191.4 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.2333 | 118 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.3333 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.6 | 24 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.6666 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 171.7333 | 92 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 213.9666 | 98 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 385.3333 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 920.3333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44 | 88 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 238.81 | 42.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1045.75 | 235 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.9166 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 212 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 23.7499 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.5 | 131 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80 | 200 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 119.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.6666 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 96.8 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.2 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.8 | 27 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 113.3333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 375 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1385.2799 | 140.4 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9422.9333 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.9167 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16 | 16 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.0833 | 85 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 47.0833 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 195.8 | 12 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 949.5 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 451.5 | 64.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1255.8333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.75 | 33 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.85 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 91.35 | 87 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 155.8 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 301.5666 | 109 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.6333 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 65.8333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 175 | 175 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 390 | 130 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3244.25 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.6666 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 315.9 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 375.4667 | 32 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 453.6 | 81 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 160.4666 | 83 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161.5 | 102 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 361.1466 | 135.43 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 669.0665 | 208 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 155.1666 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98 | 98 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.25 | 81 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 109.6333 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 127.9999 | 240 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 193.6333 | 74 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 456.1666 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 898.1349 | 114.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.2 | 14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 528.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.8 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 115 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 522.5 | 190 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 532.8 | 111 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.9 | 93 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230.0833 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1422 | 237 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2094.1665 | 350 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 891.9166 | 69.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 445.9516 | 56.93 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 528 | 66 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.4666 | 74 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.1333 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.7333 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77.5 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.5 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104.8333 | 74 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.1 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.15 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 125.0666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 424.6666 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1386.9333 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.9166 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.5333 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.3332 | 280 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 113.4666 | 74 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 122.55 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.5 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 127.9333 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 241.5833 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 428.96 | 114.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.6666 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.6 | 21 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1097.4 | 124 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.5 | 15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.1666 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 480.9166 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 650.256 | 106.02 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 59.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 82.6833 | 121 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 388.6332 | 131 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 50.4166 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.8666 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.3 | 66 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 96 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 450 | 300 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 720 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.25 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 92.25 | 205 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 102.9 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 307.0833 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1326.85 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.1666 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 71.2833 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 86.5666 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 171.1 | 118 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 397.8333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 265.9716 | 60.22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.3333 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 250 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 270.6666 | 58 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1548.3333 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1800 | 180 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 177.4499 | 117 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1435.5833 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.25 | 13 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.5 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 770.6666 | 160 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 203.66 | 101.83 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 144 | 72 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 210 | 105 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 374.99 | 53.57 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69 | 34.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.5 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 167.84 | 41.96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 880 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1230.6825 | 59.31 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 445.94 | 60.81 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7044.7328 | 842 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15135.78 | 265.54 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 271.7 | 143 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 384 | 64 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.6667 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.2833 | 101 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 262.8333 | 95 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1512.5 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1997.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13 | 13 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.4333 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174.4167 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 320.1666 | 113 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 357.5 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 379.5 | 66 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1180.8332 | 218 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48696.25 | 163 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 340 | 68 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1206 | 18 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1281.3785 | 138.03 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 329.3875 | 60.81 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 326.6666 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.05 | 69 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 260393.85 | 831 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.6 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.3333 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84.8 | 48 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130.6667 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132.4 | 66.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.9333 | 43 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.6 | 44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 244.3833 | 68.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 160 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.55 | 9 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85 | 85 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222.6833 | 31 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 259.5333 | 68 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 274.8666 | 76 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 777 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1510.6666 | 103 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 489.9067 | 18.1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 823.9 | 107 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 318.99 | 106.33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2399.04 | 133.28 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 487.6445 | 73.33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 668.4 | 24 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 139.7333 | 64 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 494 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2221.3333 | 68 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.6667 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.4166 | 73 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.6667 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 622.8332 | 185 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5107.3333 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 306.6666 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6805.25 | 163 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 218.01 | 72.67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.6 | 38.3 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102 | 34 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 186 | 93 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 133794.3997 | 876 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 58.5 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 282.3333 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 409.5 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.9999 | 96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 280.8855 | 89.17 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 254.61 | 84.87 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 222 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 317.4999 | 150 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63.4667 | 14 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1969.5 | 202 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142.3333 | 61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 149 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.8333 | 130 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 207.9 | 154 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 279 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 708.9 | 102 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 752.4999 | 105 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1035.9333 | 82 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6168 | 144 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 275.01 | 91.67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1212.36 | 101.03 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3073.75 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.8552 | 125.06 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 816 | 102 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1436.54 | 205.22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3363.9999 | 174 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.5 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2270.8895 | 64.79 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1016.6666 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1713.0664 | 352 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.5 | 5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.5666 | 43 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.6666 | 95 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 272.9333 | 23 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 468.75 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3008 | 188 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49.8667 | 44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84 | 12 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108 | 12 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.7833 | 73 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.2333 | 58 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 204.1667 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 206.15 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246.0499 | 111 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 840 | 63 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.4133 | 174.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 103.8333 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 148.7333 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 304.2666 | 112 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1223.8 | 211 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67 | 67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.79 | 94.79 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 568.3499 | 81 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 212.49 | 70.83 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 515 | 103 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 161.25 | 215 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 193.75 | 155 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121 | 66 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 251 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 648.7833 | 67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 872.05 | 163 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1960 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6411.1666 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 141.4 | 141.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 244.35 | 81.45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 495.78 | 82.63 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 569.05 | 57 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 650 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 934.692 | 69.84 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7 | 7 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 303 | 50.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 916.6665 | 220 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5120 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 447.3333 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 45 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3756 | 6 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1291.6665 | 250 | 1 | 1 | 0358-Oil burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219.6667 | 20 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.3333 | 100 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 110.8333 | 190 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300 | 100 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5343 | 78 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 244.2 | 148 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 539 | 7 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 146.9166 | 43 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91780 | 520 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22 | 11 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.4 | 108 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 22.6664 | 340 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 26.6666 | 320 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 560 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 1486.8326 | 30.52 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2777.4998 | 330 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3172.3329 | 620 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1049.2166 | 97 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 194 | 60 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 414 | 360 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 148.75 | 85 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 528 | 352 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 272.1366 | 30.52 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 495.4413 | 30.52 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 11.418 | 19.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1307.0438 | 19.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 4346.1348 | 19.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8580 | 330 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3287.1999 | 336 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5235.45 | 57 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 93.75 | 375 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 148.5 | 330 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 265.3 | 379 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 306.6 | 292 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1031.8331 | 410 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.1666 | 55 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23 | 60 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 23.9998 | 360 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 31.8 | 318 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 317.333 | 476 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 90 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81.45 | 9 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 879.45 | 533 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.5833 | 55 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3703.6666 | 164 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 121.9999 | 366 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 479.5 | 685 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.9 | 66 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.5999 | 156 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1488.6665 | 220 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 620.7996 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.95 | 129 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1549.7333 | 118 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 65.9999 | 360 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 68 | 340 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 289.3332 | 280 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 94.75 | 379 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 186.6665 | 280 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 251.79 | 30.52 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4461.0831 | 335 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 254.25 | 565 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 93.7333 | 76 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 203.9333 | 76 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.5 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 275.7463 | 570.51 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 0 | 0 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 20.5 | 82 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 74.8 | 374 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 160 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7197.5 | 150 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 45.5999 | 342 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 126.5332 | 292 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3553.8525 | 19.03 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7056 | 588 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 999 | 60 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 447.6166 | 107 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12.6666 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 243.3333 | 50 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 126 | 360 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 225.0833 | 73 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3009.5 | 39 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 34.85 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 1190.5 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 98.7999 | 114 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 351.3333 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1921.5249 | 151.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 42.5 | 17 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1190.2567 | 20.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 35.6883 | 43.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 53.2667 | 17 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 196.0083 | 54.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 27548.3666 | 233 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 92.4 | 22 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 83.3667 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 14.65 | 58.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 13.8 | 55.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 30.2 | 30.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 31.2 | 31.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 18.97 | 54.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 549.8132 | 195.2 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 54.2 | 54.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 79.3333 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 507.3333 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 26.25 | 75 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Winter | 382.3333 | 124 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 55.35 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 172 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 277.5 | 90 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 66.5 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 224.6667 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 101.6666 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 84.05 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1721.5833 | 73 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 68.4 | 36 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 46786.8 | 72 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 448.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 897.3333 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1769.4 | 36 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 21.6667 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.1333 | 44 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.4 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.1093 | 15.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.3332 | 161 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 313.1333 | 61 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 695.1667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 980.5398 | 52.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1212 | 101 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 169.5 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2.2667 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.6 | 3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.95 | 33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 96.0333 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 106.7833 | 43 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 19.58 | 26.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 103.0749 | 176.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1500 | 300 | 2 | 2 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.6 | 48 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.15 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.5 | 94 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1183.3332 | 125 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1359.45 | 81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6000.5833 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.6666 | 160 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.6 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 236.5 | 43 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2090 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 42.6182 | 196.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 46.275 | 61.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 47.25 | 56.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1499.1 | 22.8 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1616.72 | 11.2 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 537.3333 | 104 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7657.4664 | 454 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 93.6333 | 106 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.5666 | 67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.5 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 702 | 117 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.6666 | 160 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165.75 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 285.3333 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 339.2 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 588 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 43.3333 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 11.3116 | 61.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 13.3683 | 61.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 177.6 | 22.2 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12960 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228.7999 | 156 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 20187.8664 | 454 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.9999 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.8 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.0333 | 23 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 542 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 198.75 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5175.7333 | 104 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25 | 25 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 220 | 110 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 228.975 | 64.5 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1764.6 | 51.9 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1890.9409 | 335.67 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4131 | 510 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36 | 90 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 64.6 | 76 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.6 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.75 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76 | 76 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.8 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1174.5 | 29 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3378.75 | 51 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 998.75 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1672.5333 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2465.9999 | 135 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3608.4999 | 105 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3902.1666 | 130 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 650 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 539 | 11 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 62.7831 | 376.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1382.6664 | 340 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2827.6664 | 340 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 142.9999 | 330 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.3833 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.0666 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 291.2 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 406 | 116 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 460 | 115 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1033.3333 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2383.75 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.5 | 13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 443.75 | 71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1.8 | 3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.5 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 868 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1338.3333 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7104.9999 | 105 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11311.6666 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 18.135 | 362.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 29.8216 | 61.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 9.45 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 57.5167 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3291.81 | 61.3 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 327.845 | 11.9 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 626.2 | 20.2 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.8 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.6 | 88 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.6666 | 134 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.65 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2556.3499 | 129 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5800.8333 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 461.4999 | 78 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195.75 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 344.1667 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 940.8 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4560 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 27.67 | 276.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 101.805 | 61.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 140.8816 | 61.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 281.67 | 68.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.3367 | 34.1 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180.6 | 4.3 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32257.6665 | 235 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18987.9165 | 199 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.5 | 13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.2 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.2 | 13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 12.67 | 126.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44 | 22 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 374 | 6.8 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2821.5 | 13.5 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19614.7665 | 199 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 68.1166 | 67 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 650-Fluidized Bed
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 19.9333 | 23 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 650-Fluidized Bed
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 387.6667 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 650-Fluidized Bed
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 40.95 | 27.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 800-Miscellaneous
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 111.6667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 6931.6333 | 14 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 6.0967 | 11.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 50.14 | 13.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 96.6667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 8827.5333 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1.4603 | 43.81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 51.6666 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 525.3567 | 12.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 128.25 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 232.8432 | 164.36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 155.3333 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 956.0333 | 43 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3796.1 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 37.3023 | 23.81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 67.0833 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 100.3 | 34 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 15.3833 | 14.2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 39.1 | 23 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 62.6667 | 47 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1.53 | 1.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 4.8778 | 41.81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 6.7025 | 26.81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 17 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 35.25 | 47 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 249.6667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 810 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4185.9 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 14.1 | 47 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 630 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 1070 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 254.758 | 164.36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 90.3 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 93 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 274.8 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 4940.8333 | 7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 16.25 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 25 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2548 | 14 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3756.3 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 26.1392 | 44.81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 210.9286 | 164.36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 9639.3333 | 38 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 60.6666 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 35.4666 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 235.6633 | 12.2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1914.2666 | 98 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 268.2667 | 16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 792.5333 | 32 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 24.3666 | 43 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 199.7999 | 81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 66 | 13.2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 24.5 | 98 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 246 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 113.75 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 53.3866 | 45.76 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 191.3333 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 325 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 7.1666 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 31.3333 | 94 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 209.6666 | 37 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 9.6 | 16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 54.4666 | 76 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 203.2 | 48 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 339.1667 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 28.2667 | 16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 34.65 | 99 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 84 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 218.9166 | 71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 106155 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 45.5 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 240 | 16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 3165 | 211 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 32.5 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 142.2666 | 97 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 628 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 25.2833 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 146.9167 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 21.3 | 71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 183.7666 | 74 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 43.9999 | 165 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 193.8 | 76 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 32.1167 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1118.8853 | 61.76 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1672.5333 | 32 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 498.7999 | 174 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 81 | 1 | 1 | 0362-Burner tilts | D1-Forced - Immediate | 100-Fossil-Steam
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46 | 12 | 1 | 1 | 0362-Burner tilts | D1-Forced - Immediate | 100-Fossil-Steam
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17763.833 | 530 | 1 | 1 | 0362-Burner tilts | U1-Forced - Immediate | 100-Fossil-Steam
0365 | Bed warmup burners (FBC only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 38553.7333 | 136 | 1 | 1 | 0365-Bed warmup burners (FBC only) | U1-Forced - Immediate | 650-Fluidized Bed
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 29.6667 | 20 | 2 | 2 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 39.75 | 47.7 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 417.3333 | 20 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 5.885 | 10.7 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 81.3833 | 25.7 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 162.24 | 50.7 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 592.62 | 35.7 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 98.46 | 54.7 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 174.105 | 47.7 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.865 | 20.7 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 8 | 60 | 1 | 1 | 0366-Duct burners (FBC only) | U1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Summer | 1424.8333 | 166 | 1 | 1 | 0366-Duct burners (FBC only) | U1-Forced - Immediate | 851-CC GT units
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Winter | 30.2033 | 53.3 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 852-CC steam units
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2.1 | 42 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 852-CC steam units
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 5.5 | 55 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 622.5 | 150 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 53.952 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 115.2 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 287.808 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 851.2 | 56 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 274.1667 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 432 | 15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 62.976 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 73.152 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 97.728 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 116.736 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 844.032 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 1194.656 | 35.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 2011.024 | 35.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 474.0773 | 30.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 628.6665 | 410 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 17514.3164 | 397 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.3333 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 616 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.2333 | 154 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 23 | 69 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 9.216 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 13.44 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 23.808 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 30.0113 | 30.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 94.734 | 210.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1244.5 | 57 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 645.9997 | 510 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 183.1749 | 129.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 266.0665 | 307 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 160.9998 | 345 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 98844.3998 | 732 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1173.2025 | 445.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.8 | 24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 2361.216 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1598.2306 | 30.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2268.6533 | 30.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 604.1966 | 189.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 327.7 | 113 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2266.8331 | 670 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2823.4333 | 142 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345 | 115 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2012.5 | 115 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49.3783 | 27.95 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 109.14 | 96.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 875 | 350 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 29.76 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 134.4 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 326.564 | 30.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 2362.176 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 451.52 | 265.6 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3507.5 | 610 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 247.1999 | 144 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5180.3662 | 667 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 1124.8332 | 397 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.5333 | 118 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.7333 | 88 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.75 | 15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.4 | 108 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2622 | 570 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 26.112 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 537.408 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1024.1 | 209 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1841.7331 | 727 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 182.25 | 135 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 585.15 | 249 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 713.5835 | 213.01 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39577.4864 | 338.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 383.7664 | 397 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 974.1666 | 175 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5808 | 220 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95.3333 | 104 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.7997 | 468 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 148.8666 | 154 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 199.7998 | 324 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 398.208 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 5470.656 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 112.2773 | 210.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 850.4906 | 30.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3108.7332 | 442 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 737.5331 | 299 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1346.3331 | 577 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 107.136 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 2093.76 | 11.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 19.2 | 72 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1171.4593 | 30.52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 175.4666 | 112 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 10.85 | 31 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 349.0665 | 187 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 224.2 | 76 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 28.25 | 113 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 7000.4332 | 397 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 800 | Miscellaneous | MRO | Winter | 5.6733 | 14.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 800-Miscellaneous
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 18 | 30 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 800-Miscellaneous
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 11.2 | 32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 800-Miscellaneous
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 223.2666 | 68 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 82.5683 | 46.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 260.2666 | 122 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 5 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 161 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 217.5 | 10 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 391.6667 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 41.25 | 25 | 3 | 3 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 83.3333 | 125 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 350 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 20.06 | 10.03 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 89.9 | 87 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 524 | 131 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 303.3333 | 28 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 60.8253 | 37.24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | SERC | Summer | 6.475 | 64.75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | SERC | Summer | 11.8708 | 64.75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 65.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | SERC | Summer | 783.2 | 22 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 198.3333 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 12.7083 | 152.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 15.25 | 152.5 | 1 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 73.225 | 151.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 59.8 | 138 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 153 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1845.5 | 30 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 10.1666 | 152.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 44.8 | 64 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 59.9999 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | RFC | Winter | 561.2 | 12.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1511.1 | 54 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 17.0833 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 41.85 | 27 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1063 | 15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 17.7916 | 152.5 | 1 | 3 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 48.2916 | 152.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 127.0833 | 152.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 234.825 | 151.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 66 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | RFC | Winter | 6.56 | 8.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 12 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 43.25 | 15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 36 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 136.1666 | 95 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 58.9333 | 26 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 125.25 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 582.0416 | 152.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1868.3332 | 147.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 8 | 48 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 55.5 | 15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 166.75 | 145 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4236.3333 | 71 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 105.4167 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 196.5 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 659.6333 | 77 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 156.25 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 459.7333 | 64 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 146.3 | 77 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 955.3333 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 20.3333 | 152.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 447.3333 | 152.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 234.1667 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 291.4999 | 159 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 368.9 | 238 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 441.0416 | 91.25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2062.3333 | 115 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 118678.1162 | 703 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4318.9999 | 420 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 193.0998 | 579.3 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46.5 | 45 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1156.25 | 185 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 59 | 59 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138.7 | 57 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1143.95 | 167 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 399.6665 | 220 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45138.7996 | 588 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1530 | 600 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 267.4 | 382 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 543.2 | 97 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.3333 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 692.9998 | 270 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.75 | 59 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.8666 | 136 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.8666 | 28 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 338.3333 | 175 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8861.6658 | 1300 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135.2 | 78 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3974.9994 | 900 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 404.1665 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 878.7499 | 285 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 167.4999 | 150 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 535.8 | 114 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 19.8333 | 14 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 37.7166 | 73 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 106.1666 | 130 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1658.3332 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 400.0247 | 510.67 | 1 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 216.4664 | 382 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 560 | 200 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48.3333 | 145 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 303.3332 | 182 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 666.4999 | 186 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.8333 | 50 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1681.25 | 125 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 7.4667 | 14 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 25.8333 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 134.1666 | 175 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1139 | 335 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.4499 | 81 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116 | 48 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 314.6665 | 590 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 546 | 182 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.664 | 59.72 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.3666 | 86 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 61.2 | 153 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11874.4998 | 510 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 487.35 | 361 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3342.7995 | 732 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 328.4586 | 59.36 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.4166 | 71 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 230.9166 | 85 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2220.6333 | 217 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.9 | 33 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160.6332 | 158 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1123.4 | 123 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6969.9997 | 510 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3554.9995 | 1350 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4851 | 588 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1675.4664 | 412 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 1733.312 | 59.36 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 146.25 | 195 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197.4999 | 237 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 208.5417 | 12.5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1057.0375 | 205.25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1157.1665 | 262 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.8333 | 7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.6333 | 178 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.3333 | 130 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.3 | 57 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 579.3333 | 55 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 248 | 155 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 212.4096 | 579.3 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 910.5416 | 102.5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 650-Fluidized Bed
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 12.6666 | 40 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11.3333 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 26 | 40 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 610 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 193.95 | 27 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 378.3333 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | SERC | Winter | 50 | 60 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207.4333 | 98 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21 | 21 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.9066 | 38.8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111.402 | 123.78 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 134.4158 | 70.13 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1553.9 | 379 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.72 | 88.4 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 208.5333 | 68 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31500 | 600 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.3333 | 55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.8333 | 34 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.1666 | 37 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 883.3332 | 200 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 535.02 | 178.34 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.3333 | 127 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 514 | 257 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.2 | 77 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1000.1666 | 170 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.5 | 15 | 1 | 1 | 0385-Igniters | D3-Forced - Postponed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1134 | 420 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1867.5 | 415 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1230.1666 | 121 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 68.6666 | 103 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8.6333 | 74 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 110 | 22 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169.6213 | 79.51 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.25 | 45 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.5 | 275 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79.9166 | 137 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6880.8 | 732 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1002.4163 | 523 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 148.8 | 144 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290.9666 | 58 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 430 | 120 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.75 | 75 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 541.8666 | 128 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 75.8332 | 325 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 153 | 85 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3611.6135 | 598.61 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 717.5 | 410 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 552.9333 | 116 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1200 | 60 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3 | 30 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.3333 | 62 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64 | 64 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.0666 | 88 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1153.1664 | 370 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 287.9999 | 108 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 160.4166 | 125 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.8 | 68 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276.2832 | 137 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.4166 | 53 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.15 | 9 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 102.2 | 292 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 434.2833 | 36.7 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 140 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18.4999 | 111 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 324.6497 | 453 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2728 | 220 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 790.533 | 539 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25.7833 | 119 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.4 | 57 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216.6666 | 130 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.5 | 126 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 304 | 160 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 181.3332 | 340 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34 | 170 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37.9999 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117 | 195 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 80.5 | 69 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 563.6665 | 380 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.3 | 58 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1066.4 | 124 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 237.5 | 250 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1666.6666 | 100 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 220.8 | 192 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 235.4999 | 90 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4445.1331 | 598 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 280.5 | 330 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2133.4333 | 58 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 63208.65 | 83 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 63.6 | 72 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 851-CC GT units
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 419.9999 | 180 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 444 | 222 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 221.5383 | 111.7 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640 | 160 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 343.5 | 229 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 403.9533 | 76.7 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.3333 | 100 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 369.9333 | 124 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 335.6666 | 95 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 490 | 245 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.8 | 72 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89 | 15 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.5 | 74 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68 | 68 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3475.7333 | 196 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.5 | 15 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48 | 48 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 209.9999 | 126 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 19755.8664 | 427 | 1 | 1 | 0390-Burner wind boxes and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1526.25 | 165 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85 | 100 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 460 | 46 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3494.1 | 613 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 162.1833 | 37 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 108.5333 | 74 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276.5 | 79 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7904.6332 | 266 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1808 | 80 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160110 | 540 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 812.35 | 77 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17787.15 | 261 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287.9499 | 132.9 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 766.3 | 158 | 1 | 1 | 0400-Burner wind box fires | D2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21698 | 380 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114 | 12 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1099.9999 | 150 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6577.0166 | 167 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.5 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 12.65 | 25.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 31.05 | 20.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 36.7867 | 24.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 71.0233 | 28.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 12.2717 | 19.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 37.2167 | 29 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 62.2533 | 23.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 3297.165 | 20.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 350.0665 | 178 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.6667 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 791.6665 | 250 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 41.5166 | 26.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 51.04 | 23.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 40.745 | 28.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 66.8 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 159.2333 | 28.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.75 | 85 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 33.48 | 24.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 43.815 | 20.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 67.28 | 23.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 135.2 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 72 | 6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 57.0467 | 19.9 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 133.75 | 107 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175.5 | 117 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2330 | 100 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.9166 | 55 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 85.6 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 119.8666 | 31 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 34.6567 | 28.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 112.4933 | 23.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 132.24 | 26.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 14146.1332 | 349 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.3332 | 200 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 766 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3379.3332 | 137 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85.9999 | 120 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 368.25 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 61.9666 | 28.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 25.38 | 14.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 60.52 | 26.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 98.25 | 15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.0833 | 175 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166 | 120 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1673.25 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 18.4333 | 15.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 16.56 | 20.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 40.4 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 115.6133 | 23.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 200.2 | 28.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 402.4166 | 219.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18049.9998 | 600 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 572.2999 | 177 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1492.25 | 127 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 44.6966 | 25.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 27.945 | 20.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 120.28 | 24.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 134.2666 | 26.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 191.7867 | 24.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 226.0933 | 24.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 26.7 | 178 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 832.8833 | 77 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 22.575 | 21.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 26.1 | 29 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 98.3733 | 24.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1107 | 410 | 1 | 1 | 0410-Other burner problems | SF-Startup Failure | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 408 | 68 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 650-Fluidized Bed
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 245 | 28 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 650-Fluidized Bed
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 58 | 58 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 650-Fluidized Bed
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 616 | 28 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 650-Fluidized Bed
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 822.5 | 15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 273 | 273 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 494.4998 | 258 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 177.45 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 55 | 1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1.8 | 36 | 1 | 6 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 47.7333 | 16 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 62.1833 | 91 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 94.5 | 70 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2.4 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | SERC | Summer | 387.7333 | 32 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 0 | 0 | 1 | 4 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | RFC | Winter | 134.1267 | 6.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 0.59998 | 36 | 1 | 3 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 163.3332 | 200 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 14.5667 | 19 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1.6 | 6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1.2 | 36 | 1 | 6 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 49.8 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 20 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 27.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158.01 | 52.67 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 347 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 698.75 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.6667 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.4166 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.5833 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 458.35 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4.6666 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 7.2 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50.4267 | 24.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 65 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1176 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 250 | 25 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1080 | 45 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.18 | 49.8 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 4.1666 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 12 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 14.7333 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.8333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 288 | 72 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 449.5833 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 101.6667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 270.8333 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 327.75 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 630 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1188 | 108 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4.1666 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5.0667 | 38 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 9.5 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11.6666 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 21 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.3333 | 77 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.7667 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 63 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 140.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 284.2542 | 40.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 586.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117 | 45 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 466 | 120 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 16.6667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.6667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.539 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.2 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.4333 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 230.4166 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255.3 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 263.3333 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 481.6667 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 610 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 680.8333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 767.25 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1582.9332 | 212 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.3955 | 1.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 13.3 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 33 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 278.25 | 105 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 576 | 120 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1801.6666 | 92 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70 | 84 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.8165 | 2.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 17.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.1667 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 188.4166 | 119 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 271.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 362.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 444 | 37 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 649.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 10.1333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32 | 6.4 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.5 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69.7833 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.13 | 75.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 391 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 429 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 883.4833 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.9665 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15.2 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 32.6833 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108 | 27 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156 | 16 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 157.5 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 293.9999 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 360 | 120 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.0833 | 55 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164.3333 | 58 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137.78 | 49.8 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3897 | 10.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 230.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2182.0166 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.8 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.4 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 470.3333 | 166 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.2155 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12.6667 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 32.2667 | 4 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 42.4666 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 45 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 128.3333 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 220.8333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4132.2666 | 104 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 24.3333 | 73 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 280 | 20 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 374.78 | 26.77 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 58.2667 | 38 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.94 | 43.3 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 467.5999 | 84 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 25 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 275.9999 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 332.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3707.6 | 46 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4 | 24 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 114.3 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 126.5 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.6666 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 7.6 | 38 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14.9333 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 16.8 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 53.75 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 68.9 | 78 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 742.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 811.8 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24 | 6 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 377.65 | 49.8 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6871.7329 | 584 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 77.715 | 47.1 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 11.6666 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 43.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 156.6667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 172.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 674.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8775 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.75 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.03 | 51.48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.2 | 56 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 108.64 | 29.1 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 591.04 | 36.94 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 774.8 | 52 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1441.3333 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1.25 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 352.0833 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 719.25 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 411.6666 | 52 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 303.4 | 74 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.495 | 43.3 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.2 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35 | 17.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4723.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5530.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1.0043 | 30.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32.4 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48.3333 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 768 | 51.2 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4282 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 6.3333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10.1333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12.6 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.0833 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 135.9167 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 198 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 222.2499 | 105 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 860.4166 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1084.45 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 126.0833 | 89 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 37.1 | 53 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2514 | 120 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 192.5333 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 53.95 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 20305.9999 | 429 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 23845.0164 | 439 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 17.7333 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 11146.8499 | 429 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 59.15 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 4055.9665 | 449 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 25.9667 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 405.4498 | 459 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 14157 | 429 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 13.6667 | 20 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2773.0164 | 439 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 6087.9162 | 769 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 55.2 | 69 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 198.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 244.7998 | 459 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4.3333 | 26 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 218.1666 | 55 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 251.6667 | 25 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 71.25 | 25 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300 | 40 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 87.5 | 35 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 988.8667 | 26 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 235 | 60 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 198 | 24 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 333.3333 | 40 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 47.3 | 66 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.65 | 31 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.2 | 76 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.9667 | 1 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.3 | 101 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59 | 11.8 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.6 | 51 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 703.8333 | 41 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1084.2666 | 76 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1116.4 | 6 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1133.4833 | 47 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.8667 | 26 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.3 | 31 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.8333 | 46 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.8 | 21 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.8666 | 76 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3103.45 | 21 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.4005 | 5.13 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.4333 | 31 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.2666 | 56 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.9333 | 4 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 104.4 | 4 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 298.9333 | 16 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.25 | 51 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.6666 | 76 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.6667 | 16 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.9666 | 106 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96 | 96 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261.8667 | 16 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 575.05 | 31 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 653.95 | 41 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1420.8333 | 31 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2188.6 | 31 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.0333 | 11 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.3666 | 86 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.8 | 106 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56 | 56 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.6666 | 31 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103.5833 | 11 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.5 | 6 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140.7667 | 41 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 235.4833 | 71 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 631.1667 | 14 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2025.1 | 21 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2461.95 | 27 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 202.95 | 33 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.05 | 51 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.4667 | 16 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.4 | 51 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.5333 | 26 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.8667 | 16 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.0833 | 71 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.6333 | 11 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160.8 | 6 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.5 | 6 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 284.7 | 6 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 292.9333 | 26 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.1333 | 16 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.6 | 6 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.6167 | 41 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 336.05 | 11 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 789.4666 | 31 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1288.7333 | 26 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1694.7667 | 26 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.1 | 41 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.8666 | 56 | 1 | 2 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.7667 | 41 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.9333 | 26 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.8 | 16 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.7 | 71 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.5 | 46 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.6667 | 11 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.9333 | 136 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108 | 36 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 925.8 | 36 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 183 | 45 | 1 | 1 | 0425-Cyclone dampers | D3-Forced - Postponed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 205.85 | 69 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 7259.95 | 69 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 248.9 | 19 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 5572.7 | 419 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 167.6166 | 89 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 9603.3333 | 40 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.25 | 5 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16267.9999 | 210 | 1 | 1 | 0426-Cyclone air ducts | U1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320 | 80 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.1666 | 110 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 291.0453 | 53.24 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1413.6927 | 137.03 | 1 | 1 | 0430-Cyclone furnace | U2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1759.2329 | 593 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12050.75 | 43 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.564 | 51.48 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 234 | 36 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7254 | 585 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.4033 | 44.42 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1573.5611 | 137.03 | 1 | 1 | 0430-Cyclone furnace | U2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 9578.8666 | 212 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.5 | 110 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1370.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1808.8 | 34 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3667 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.7333 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.3333 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.5833 | 31 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.1 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4167 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.8333 | 46 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.15 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.8333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.0166 | 71 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.9333 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.15 | 101 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.8333 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.5 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.7593 | 31.13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6699.1 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.25 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4 | 30 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.25 | 45 | 1 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 45 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.3 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105.3 | 81 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 429.8167 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 533.5 | 110 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1306.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.75 | 35 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6166 | 31 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.4167 | 35 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.7166 | 31 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.2333 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.6666 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2 | 41 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.5 | 50 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.9833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.6666 | 106 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38 | 19 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.02 | 8.78 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.6 | 6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.52 | 5.13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1166 | 106 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.05 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.9167 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.1666 | 50 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 53.2242 | 49.13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.9167 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.8333 | 85 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 635.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 62.05 | 73 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1273.3333 | 50 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.25 | 85 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.1667 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.0833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.5167 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.3 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 12 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.75 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.5833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.25 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 601.6667 | 38 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 5.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.25 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.55 | 31 | 1 | 14 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.0666 | 31 | 1 | 7 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.5 | 50 | 1 | 7 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.7333 | 41 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.3333 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.25 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.1 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.1333 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.6 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.01 | 8.67 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.2666 | 106 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 364.9333 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36 | 18 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1488 | 320 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.5 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.6 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 255.2 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.2 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.5 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 96 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.25 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.0333 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.6667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.6 | 96 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.6333 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3194.1332 | 424 | 1 | 1 | 0435-Other cyclone problems | SF-Startup Failure | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.4 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.0333 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.75 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.1 | 41 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.1333 | 31 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.7833 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.9 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.5 | 51 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.3333 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 462.4166 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 17.1 | 38 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 15 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.75 | 85 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.75 | 125 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300 | 100 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.6666 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.3 | 46 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.65 | 31 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.6833 | 31 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.8333 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.75 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.8833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.6667 | 50 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.9 | 106 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.45 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.75 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 185.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 280.5 | 33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1079.1666 | 185 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2699.05 | 469.4 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 184.25 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 558.6 | 57 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4462.25 | 356.98 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4175.04 | 347.92 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8446.08 | 351.92 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 657 | 219 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 32.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 71.05 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 606.15 | 449 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 686.5665 | 479 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2126.2332 | 454 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 695 | 139 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 410.6666 | 80 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 13.3 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 126.5 | 69 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 7362.9496 | 579 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 136.5 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1069.4499 | 219 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 531.3165 | 449 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 980 | 400 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 562 | 120 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33 | 8.25 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.5 | 30 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.5 | 30 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 484 | 440 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2226.9999 | 255 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1350.0499 | 201 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 668.1 | 393 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 456.533 | 428 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1737.2 | 86 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1675.4583 | 197.5 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 850-Combined Cycle Block
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2188.368 | 260.52 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1489.3058 | 260.52 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 176.4167 | 29 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 5.5 | 22 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 564.3306 | 264.53 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 780.7026 | 165.52 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 724.9512 | 252.89 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1765.3 | 278 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 43.3333 | 130 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 53.6667 | 14 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 47765.25 | 292.5 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 898.9 | 202 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1964.25 | 81 | 1 | 1 | 0450-Fuel oil heaters | U1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 183.3332 | 250 | 1 | 1 | 0450-Fuel oil heaters | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 350 | 200 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 188.3333 | 25 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 204.6 | 31 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 841.6667 | 50 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3.05 | 3 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 43.1666 | 74 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 104.55 | 51 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2461.0864 | 333.33 | 1 | 1 | 0460-Fuel oil atomizers | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 238.3333 | 55 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 246 | 60 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 160.5 | 90 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0 | 0 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1071.6 | 36 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1272.1666 | 170 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 381.1332 | 285.85 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 208 | 38.4 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 86.1666 | 110 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 163.3332 | 140 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 4.8 | 36 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 305.8666 | 62 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2148.3333 | 50 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 66.6666 | 100 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18100 | 200 | 1 | 1 | 0460-Fuel oil atomizers | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 748.9166 | 55 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52 | 16 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 355.1833 | 101 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4987.8 | 36 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1941.4999 | 330 | 1 | 1 | 0470-Oil and gas fires | SF-Startup Failure | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 864 | 36 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4988.4 | 36 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 188.5333 | 101 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 6 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 64.35 | 143 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 945 | 36 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 281.6497 | 393 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 2009.7 | 92.4 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.3333 | 175 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.6667 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 536.6666 | 200 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 30.17 | 129.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 156.55 | 93 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 74.3166 | 91 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 613.0666 | 76 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 8506 | 60 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 479.1665 | 575 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1122.3333 | 37 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 139.7166 | 83 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 5374.6666 | 139 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 33.3 | 74 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1418.8161 | 781 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 181.2166 | 83 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1243 | 60 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6579 | 255 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5225 | 150 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432.6166 | 101 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 115.2666 | 28 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 527.9165 | 181 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 746.9 | 194 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7932.7999 | 192 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 183 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 116.15 | 69 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5214.9999 | 150 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5355.3333 | 145 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 391.9667 | 22 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 20.1 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3224.1667 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3024.1663 | 475 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 336 | 40 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1053.5 | 43 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 649.1665 | 410 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243 | 108 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2191.75 | 33 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 162.9166 | 85 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96000 | 200 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 58.3 | 106 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1402.7 | 169 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3940.5998 | 732 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.7333 | 44 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 18.5333 | 8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 420.3 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 558.3 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 770 | 154 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 202.3499 | 171 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1451.7998 | 732 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 187.8333 | 98 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1161.3332 | 520 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 506.1 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 855 | 95 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2320.5 | 102 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22562.4 | 816 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 12 | 9 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 12209.45 | 33 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Summer | 24550.9 | 33 | 1 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 14949.1757 | 232.07 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 104.4999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 112.1 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1674.8292 | 273.07 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 100.7 | 114 | 3 | 4 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 269.7999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 139.2 | 69.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133.7333 | 59 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 273 | 39 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 386.8333 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 500 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 645 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.6667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 120.3333 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 152 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 370.5 | 39 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 779 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1305.5 | 42 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 837 | 620 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12531.3497 | 507 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29496.083 | 485 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 270.4 | 39 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 337.5 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1128.75 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2236 | 39 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2667.5 | 55 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 462 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 505.5 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 406.8333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 700 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 837.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2083.5 | 54 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3097.0667 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 132937.3666 | 163 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21060 | 1350 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 28236 | 390 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4995.5 | 485 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 347.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 358.3333 | 43 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 400 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 536.6667 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 550 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 678.5 | 59 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 189 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 258.6667 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 502.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 642.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1125.6 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2053.3331 | 550 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7002.9 | 93 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9909.6665 | 620 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 297 | 44 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 471 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1085 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1530 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 247.5 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1530.6667 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1550 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8776.8 | 414 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 54692.9998 | 540 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175 | 50 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 192.5 | 55 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 451 | 41 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1869 | 42 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2844 | 36 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2256 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3147.0832 | 415 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10557 | 414 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4884 | 110 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 165 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 189.75 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 261.5832 | 215 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 360 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 700 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1145 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1583.3333 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2662 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 323 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 442.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 550.0833 | 41 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 267.6665 | 220 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 237814.5 | 497 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5937.1166 | 101 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145.6667 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 495 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1706.8333 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 341.8667 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 720 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1378 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 111 | 37 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 360 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 416 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 654.5 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2010.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1239.0533 | 127.3 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 305.4333 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1638 | 36 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2221.2667 | 44 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 496 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 700 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31 | 31 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1507.8 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 173.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1884.8566 | 24.91 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 281.2526 | 272.18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 3047.5 | 265 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1224.8145 | 186.52 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Summer | 11531.25 | 125 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 8547.4999 | 195 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 1311 | 138 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4174.1 | 134 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2103.75 | 75 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 3088.6666 | 82 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 350 | 100 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2655 | 150 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.0167 | 13 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 699.1667 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13368.7499 | 225 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | SF-Startup Failure | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1666.7333 | 46 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.3333 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 861.6667 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3453.6 | 144 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 466.2 | 36 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.1333 | 59 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1787.0349 | 255.9 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 569.1667 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 95.6666 | 82 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1199.1666 | 50 | 1 | 3 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1318.6666 | 46 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1550.8333 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14855.1663 | 595 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22299.8331 | 670 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 178.85 | 5.11 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 285.1333 | 14 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320.16 | 6.67 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1166.55 | 231 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 436.3332 | 170 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 836.5 | 70 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1617 | 70 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2586.5 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70 | 120 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 264 | 132 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 809.55 | 257 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78416.6665 | 500 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13833.81 | 565.8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 409.8166 | 67 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1658.1067 | 20.8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215.8333 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 405 | 270 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 620 | 310 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1368 | 144 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.91 | 1.8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14260.74 | 46.8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.5 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 606.6667 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1198.3333 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 78 | 26 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2090 | 55 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6709.0833 | 55 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1199.1666 | 50 | 1 | 3 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 132.5666 | 82 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 333.5498 | 285.9 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 210.2333 | 119 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 13939.3332 | 280 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1152 | 128 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 1190.7999 | 78 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 518.75 | 15 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 850-Combined Cycle Block
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 375.4165 | 265 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 850-Combined Cycle Block
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 362.5 | 25 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.25 | 15 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 314.3833 | 13 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 226 | 113 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1098.5333 | 107 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2108 | 80 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35470.9998 | 474 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3454.1665 | 250 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13685.7 | 1029 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25237.3332 | 364 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6389.1665 | 410 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5.0667 | 3.8 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1440 | 240 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.3333 | 44 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 393.75 | 315 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3202.7998 | 306 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Winter | 198.0299 | 289.8 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15510.3329 | 620 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 854.05 | 19 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 962.4997 | 750 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2674.6 | 622 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 404.55 | 9 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11146.3331 | 595 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34318.5998 | 732 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 50390.9996 | 540 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 72.5007 | 228.95 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27187.5 | 750 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65521.25 | 1325 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.3667 | 19 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1269.9166 | 311 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1883.3332 | 250 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24424.1661 | 790 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 183.5399 | 289.8 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 5015.7166 | 151 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 24465 | 525 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 198.1 | 283 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 22104.2499 | 255 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 202.8165 | 283 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1327.0832 | 162.5 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 68.2732 | 146.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 116685.66 | 168.56 | 2 | 2 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 536.4332 | 146.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 403.3333 | 110 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 52.2666 | 112 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 407.1167 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1519 | 35 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3142.4 | 32 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.7333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.9667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.4833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.8 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.9167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300.9167 | 23 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1405.8333 | 70 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2056.5999 | 78 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2098.2 | 78 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31709.9997 | 450 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.5 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96.2 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.3 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.5333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.75 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.7333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.4667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.1333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.4667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.5 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.75 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1235.6667 | 22 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 709.8 | 78 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 640 | 32 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.75 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.1333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.6 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86 | 43 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 354.9999 | 300 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.55 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.5333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.0833 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9319.5 | 570 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.7 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.5333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 494.6666 | 70 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.5333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.55 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.2667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.95 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.5833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.1833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.83333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.3667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.2333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1992 | 415 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.2667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.4 | 4 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.05 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.5 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.8 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.5667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80.5333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.2 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.5333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61.8333 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 104.8 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5858.3333 | 190 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4296.9831 | 311 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1421.6666 | 50 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.8333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.1 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.8 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.7667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.9166 | 25 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.5667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.35 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.75 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.5 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.6667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.0667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.3667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.65 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.45 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.1 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.4167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.1 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.5 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.7333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.4 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.1667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.1 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.1 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40.1333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43.8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 467.9999 | 135 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2892.1664 | 469 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1400 | 50 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25685.8329 | 650 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.4167 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1110 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.2667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.3 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.7 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.9333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.5833 | 5 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.8 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 632.6667 | 26 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.8 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78.45 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 561.75 | 21 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2880 | 800 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | SERC | Summer | 1672 | 66 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 800-Miscellaneous
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 6.3 | 27 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 12767.745 | 47.9 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14 | 1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24 | 6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 86.6667 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13 | 1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.75 | 13 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128 | 16 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 335.3333 | 8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 468.75 | 5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88 | 11 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97 | 30 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 390 | 15 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8 | 8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D3-Forced - Postponed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12411.8166 | 191 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 3965.4299 | 289.8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4 | 1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15 | 1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67 | 4 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1015 | 7 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39 | 13 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77.5 | 15 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144 | 12 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200.3333 | 4 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 345.8333 | 125 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13256.6664 | 328 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 125 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 256.5 | 9 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12 | 2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 11 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.4167 | 13 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 439.25 | 15 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 314.6667 | 16 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.3333 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D3-Forced - Postponed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40 | 8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.6 | 9 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11 | 11 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12 | 3 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 9 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110 | 2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182 | 14 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 504 | 18 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 27510 | 786 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10224.0666 | 251 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3154.4999 | 270 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18 | 6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51 | 6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 286.6667 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 768.3333 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 671 | 11 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 6631.5899 | 289.8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.5 | 6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103.3333 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 376 | 8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1548 | 9 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1 | 1 | 1 | 2 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10 | 10 | 1 | 3 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.8 | 4 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1706.6667 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6096.5998 | 324 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 375 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D3-Forced - Postponed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16 | 4 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.5 | 9 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115 | 5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1023 | 18 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D3-Forced - Postponed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 185106.0665 | 404 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 3501.3332 | 260 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D2-Forced - Delayed | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 17272.5485 | 286.84 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Winter | 1394.5666 | 39.1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 67886 | 149.2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 19976.3665 | 181 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Winter | 1245.6 | 34.6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 44317 | 97.4 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 11036.6666 | 100 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 482884.9999 | 358.8 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | SF-Startup Failure | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5217.3833 | 229 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 57.96 | 289.8 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.5 | 306 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 836.8833 | 67.4 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11581.2663 | 598 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1322.5 | 50 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 620.7999 | 192 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 35178 | 165 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 487.983 | 437 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2015 | Gas | GG | 851 | CC GT units | SERC | Winter | 2108.75 | 175 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U3-Forced - Postponed | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 1054.7999 | 216 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 587.6666 | 215 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 9933.6649 | 183.9 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 1578.55 | 131 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D3-Forced - Postponed | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 913.7915 | 227.5 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 11300.2865 | 209.2 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 9409.4 | 286 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | SF-Startup Failure | 852-CC steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 75.1333 | 28 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2550 | 10 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2610 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4700 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 208 | 8 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 182.5333 | 37 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4182 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49315.2 | 9.6 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 255 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5052.5 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2331 | 37 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18262.1661 | 790 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 14 | 7 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 800-Miscellaneous
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 236.25 | 15 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 383.5066 | 164.36 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2005.0332 | 182 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 552.0665 | 196 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 957.1333 | 196 | 2 | 2 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 692.5333 | 196 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 819.3832 | 233 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1421.3 | 233 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.6666 | 70 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3458.8665 | 307 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | RFC | Winter | 1475.3866 | 290.24 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.45 | 9 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 3668.3332 | 310 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 650-Fluidized Bed
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 5811.1666 | 293 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 650-Fluidized Bed
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 288.83 | 339.8 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 436.9999 | 285 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 4924.9995 | 750 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 492.1433 | 154.6 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | MRO | Summer | 5505.5 | 154 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 247.36 | 154.6 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 591.0832 | 173 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | MRO | Summer | 1655.5 | 154 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 92.6566 | 146.3 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 179.1999 | 168 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 38.9666 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 145.8 | 162 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 676.5 | 165 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 10920 | 40 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 536.8 | 176 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 176 | 110 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 350.1666 | 110 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | MRO | Summer | 4039.75 | 113 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 36.8666 | 158 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 16328 | 40 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | MRO | Summer | 2429.5 | 226 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 75.6 | 84 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 70.9333 | 112 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 4542.3666 | 127 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 310.9166 | 91 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 168.5332 | 158 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1501.0574 | 295.29 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83 | 30 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 1434.51 | 289.8 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66729.4993 | 1110 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 540 | 270 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 946.4 | 169 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 677.1666 | 170 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 291.8332 | 170 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 206.25 | 75 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 537.6 | 96 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 308.2666 | 136 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 4865.5833 | 95 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 965.6 | 136 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 490.9665 | 286 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.5833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.7333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.1667 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.2667 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.3 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 2.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.3 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10134.1332 | 427 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.4 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.3333 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 120 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 162.5 | 130 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.6 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4 | 2 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.3833 | 19 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.3333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135 | 9 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.75 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.75 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.8333 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.9 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.95 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.7333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.5833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.8 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.6 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.2 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 515876.4 | 58.89 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 18 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10362.6 | 513 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.6667 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.4 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.9 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.25 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.4333 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.6167 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.86666 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66.96 | 7.44 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.7667 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22 | 110 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.6 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.2333 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.2 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.5 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.5333 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 436.6083 | 43.3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5 | 5 | 2 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.8333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.75 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.4 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.9333 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.1667 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.5 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2311.619 | 292.61 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110 | 10 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203 | 29 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 780 | 20 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 489.8 | 316 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4333 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.25 | 14.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.3 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1722 | 140 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.65 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.1667 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.3333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.1667 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.4833 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.25 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.2 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.5 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 106.5167 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15309.9996 | 600 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1594.6663 | 598 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197.7666 | 34 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 254.9583 | 14.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.63333 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.85 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.4 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.8 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.7 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.6 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.1 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.6 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.9167 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.6667 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 445.2 | 159 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 234.72 | 14.4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22581.1832 | 427 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | SERC | Summer | 301.4 | 66 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 800-Miscellaneous
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 7857.3 | 66 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 800-Miscellaneous
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | SERC | Summer | 6751.8 | 66 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 800-Miscellaneous
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 666 | 333 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 5333.4166 | 287 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 1374.8666 | 164 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Summer | 2.8099 | 168.6 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 1716.5332 | 164 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 3700.3999 | 174 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Summer | 8.43 | 168.6 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | MRO | Summer | 3069.85 | 147 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 863.4833 | 103 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2805.0665 | 268 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 361.5333 | 68 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1112.4 | 103 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 861 | CoG GT units | WECC | Summer | 9850.5 | 495 | 1 | 1 | 0570-Other reheat steam problems | U2-Forced - Delayed | 861-CoG GT units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1987.5 | 150 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15840 | 330 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 626.25 | 167 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1709.8 | 103 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2308.8 | 96 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3600 | 240 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19.4333 | 106 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1382.0833 | 31 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16275 | 300 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 186.4333 | 119 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 640.2 | 388 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 981 | 60 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 831.8333 | 62 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4602.9331 | 336.8 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 459.9999 | 300 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1820.4 | 222 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2155.9999 | 294 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1584.3666 | 149 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 198 | 99 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.3333 | 20 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1451.25 | 75 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.5 | 175 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 980 | 150 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1138.9166 | 173 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12141.5 | 35 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 300 | 100 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1120.6498 | 279 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3471.3665 | 446 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6326.6865 | 306.13 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 536.97 | 76.71 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17940.2131 | 336.8 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.7417 | 14.5 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 957.7666 | 118 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4365.7 | 298 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1617.0998 | 471 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1065.4666 | 122 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7333.6999 | 339 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 525 | 100 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12942.8331 | 790 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 564 | 80 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3129.0998 | 498 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 610.8666 | 154 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14045.8999 | 339 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3632.1662 | 703 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1828.1997 | 396 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38 | 40 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 4167 | 9 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1469.85 | 9 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 36.6666 | 50 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1057.6667 | 20 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 33400 | 50 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5035.7 | 37 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3825.0664 | 352 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1404 | 468 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3220 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7250.4 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 672 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D2-Forced - Delayed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 38026.9333 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D3-Forced - Postponed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3653.3 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 374563.5 | 670 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 891.45 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2.4 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 606.6666 | 200 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 487.6667 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D2-Forced - Delayed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 0.11666 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D3-Forced - Postponed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 17238.1333 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D3-Forced - Postponed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3024 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D3-Forced - Postponed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 804.75 | 37 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 106.4 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30.9167 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 63.7333 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 720.1833 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3824 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D3-Forced - Postponed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3711 | 30 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26 | 30 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11.4667 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7876.033 | 554 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1443.05 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1568 | 7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D3-Forced - Postponed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26.6667 | 50 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2909.565 | 74.7 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D2-Forced - Delayed | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14869.5829 | 635 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 729 | 270 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40370.75 | 595 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4676.1996 | 618 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3900 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 7871.7215 | 598.61 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 587.4997 | 750 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22553.3 | 638 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8799.9996 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 103299.9996 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20658 | 330 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 337.0293 | 48.61 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32234.1 | 773 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 10492.297 | 466.67 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24849.4663 | 577 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2555 | 511 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21598.5 | 770 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46110 | 424 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 691.6666 | 100 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14634.9 | 606 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7196.6665 | 635 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41513.3329 | 650 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8161.4163 | 595 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1399.9994 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 12.2033 | 36.61 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6186.6664 | 800 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 8360.5859 | 598.61 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10767.3329 | 620 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22777.9994 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.3 | 31 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8785 | 700 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 11299.6955 | 596.29 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54938.3331 | 850 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65289.1497 | 783 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3681.9997 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5502 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1265.3332 | 520 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1007.9999 | 432 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70230.5998 | 297 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30499.7332 | 424 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 17849.4 | 419 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5520 | 240 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 19814.5662 | 769 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20510.5 | 635 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 471.75 | 9 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19660.6662 | 766 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U2-Forced - Delayed | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 3471.3 | 495.9 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U2-Forced - Delayed | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7438.5 | 783 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 645.6666 | 149 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14529.6665 | 455 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3998.8498 | 477 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5842.4098 | 541.8 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6908.7666 | 203 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9120.5 | 290 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22381.3328 | 770 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7340.6664 | 770 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1761.5 | 542 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 256.4 | 128.2 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1027 | 395 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1854.6666 | 260 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 913.92 | 57.12 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 170.01 | 56.67 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2161.08 | 60.03 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1126 | 56.3 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 601.6665 | 380 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 616.9499 | 81 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Winter | 216 | 180 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Winter | 29760 | 40 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Winter | 873.6 | 36 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 546 | 21 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 247.9 | 67 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 8184 | 11 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 193.2 | 276 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 675 | 18 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.5 | 134 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41421.6827 | 881 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2562 | 12 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9836.6664 | 454 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36.575 | 28.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5668.483 | 539 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1597.0666 | 113 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 4024.35 | 99 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1362.8333 | 130 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4340.0999 | 207 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 108870 | 60 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1413.3333 | 100 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 864.6 | 18 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 494 | 130 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 334.9998 | 300 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 2798.9332 | 128 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23262.7163 | 577 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10815.5 | 485 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 123.5 | 13 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 800-Miscellaneous
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 4161.15 | 27 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 134 | 134 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1702.4166 | 155 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | SERC | Winter | 465.96 | 155.32 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 9000 | 225 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 1400.0166 | 167 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1207 | 170 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2790 | 225 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 79.6596 | 154.18 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Winter | 245.05 | 169 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 145 | 100 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 902.885 | 107.7 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 712.5 | 75 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D3-Forced - Postponed | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 5838.1 | 147.8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1832.72 | 147.8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1647.4999 | 150 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 570.3329 | 590 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420 | 120 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1996.1665 | 590 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2369.9999 | 225 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3058.1 | 577 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13650 | 600 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 1243.5 | 45 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1080 | 120 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 469.0498 | 477 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1063.3333 | 44 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1105 | 260 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D2-Forced - Delayed | 850-Combined Cycle Block
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1187.3332 | 260 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D2-Forced - Delayed | 850-Combined Cycle Block
0700 | Blowdown system valves A | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7021.6666 | 55 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16896.1329 | 602 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32207 | 602 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3322.8 | 156 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5029 | 235 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1600 | 200 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32346.4329 | 713 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12328.4 | 196 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2395.7411 | 137.03 | 1 | 1 | 0700-Blowdown system valves A | U3-Forced - Postponed | 100-Fossil-Steam
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 218.8166 | 262.58 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4054.5499 | 249 | 1 | 1 | 0700-Blowdown system valves A | D3-Forced - Postponed | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1370.6 | 154 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 4004 | 154 | 1 | 1 | 0700-Blowdown system valves A | U2-Forced - Delayed | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 26.8333 | 70 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1018.9666 | 154 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1984.7 | 223 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1475.5165 | 223 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 978.0333 | 37 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4509.5699 | 335.7 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2542.5 | 113 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 440.5332 | 236 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3820.3333 | 157 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4436.6332 | 334 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5337.3666 | 113 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6153.5833 | 55 | 1 | 1 | 0710-Blowdown system piping B | U3-Forced - Postponed | 100-Fossil-Steam
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 21746.2496 | 675 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2541.4249 | 258.45 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 15126.2333 | 214 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 12157.5333 | 172 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 2066.7 | 166 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2644.8 | 174 | 1 | 1 | 0710-Blowdown system piping B | U3-Forced - Postponed | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1120.5 | 90 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1565.6 | 103 | 1 | 1 | 0710-Blowdown system piping B | D3-Forced - Postponed | 852-CC steam units
0720 | Blowdown system controls / instrumentation | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 260 | 13 | 1 | 1 | 0720-Blowdown system controls / instrumentation | D1-Forced - Immediate | 800-Miscellaneous
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 177.8 | 254 | 1 | 1 | 0720-Blowdown system controls / instrumentation | SF-Startup Failure | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 109.6332 | 253 | 1 | 1 | 0720-Blowdown system controls / instrumentation | SF-Startup Failure | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 164.4999 | 282 | 1 | 1 | 0720-Blowdown system controls / instrumentation | SF-Startup Failure | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 143.5 | 287 | 1 | 1 | 0720-Blowdown system controls / instrumentation | SF-Startup Failure | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 411.3666 | 287 | 1 | 1 | 0720-Blowdown system controls / instrumentation | SF-Startup Failure | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 156.6332 | 254 | 1 | 1 | 0720-Blowdown system controls / instrumentation | SF-Startup Failure | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 286.6832 | 167 | 1 | 1 | 0720-Blowdown system controls / instrumentation | U1-Forced - Immediate | 851-CC GT units
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32797.4166 | 185 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 21033 | 540 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1352.1667 | 10 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3456 | 192 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 3635.9998 | 540 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1178.9998 | 540 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 20.7833 | 43 | 1 | 1 | 0730-Other blowdown system problems | D2-Forced - Delayed | 852-CC steam units
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4080 | 170 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10505.15 | 51 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3355.2 | 24 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 26.6666 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 47.4999 | 150 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 57.4999 | 150 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 3706 | 120 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 216 | 45 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 372 | 372 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 788.2332 | 442 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 35612.5 | 259 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.5 | 30 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 234 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 24880.7666 | 142 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 50955.7166 | 97 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7007 | 245 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19152 | 608 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5063.6666 | 110 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360.8 | 132 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 93434 | 682 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3442.25 | 35 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 58.5 | 195 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 4257.5 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 4768 | 120 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2919.8666 | 122 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 665.6 | 24 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 773.8291 | 57.25 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22730.3328 | 740 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.5333 | 18.8 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9325 | 50 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3600 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4872.9166 | 125 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2165.3333 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38522.1666 | 53 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 56 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 66.6666 | 200 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 102.5 | 205 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 4843.9999 | 120 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1827.0666 | 142 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1360.333 | 530 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 55023.3331 | 850 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1646.1 | 59 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6310.5999 | 83.4 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.84 | 115.2 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 30.3333 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 253 | 230 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 54300 | 100 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 20.85 | 83.4 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266.3333 | 94 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1721.2 | 24 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6305.25 | 45 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 124.6665 | 220 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1726 | 24 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 377.6665 | 515 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 789.6665 | 515 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 18009.9996 | 600 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7418.8333 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35010 | 72 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.3 | 73 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1283.0833 | 89 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 48.1666 | 170 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 715.625 | 57.25 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 627 | 45 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 18260 | 88 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1481.3333 | 88 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 6058.1166 | 103 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 4175 | 167 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 851-CC GT units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2725 | 109 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2318.8 | 49.6 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.5 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142.4 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1009.6 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.4666 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52.5 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 193.45 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 984 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1139.1666 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1203.8 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4686.5 | 91 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 54.9999 | 150 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 108 | 180 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1488.7666 | 118 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7963.75 | 69 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3313.38 | 788.9 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.2 | 48 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.6 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 195.2166 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 200.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 847.45 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7902.5 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98260 | 170 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.05 | 61 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.2 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.0666 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.1 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43.2833 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 122 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 29629.8 | 324 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 441.9999 | 408 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14628.8 | 446 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 207.1333 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220.8333 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 973.6 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1060 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.6667 | 20 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.3333 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.8666 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44.1666 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55.65 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 522 | 87 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1391.8166 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1941.3332 | 140 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25293.2998 | 531 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.5333 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.65 | 49 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 306.9 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.1333 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.25 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 162 | 81 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 257.9333 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 419.8833 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 485.3333 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 760.8 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 955.6666 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1224 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1372.5 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1450.7833 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 11934 | 117 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4666 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.6 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.8 | 54 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 224.1 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 432 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1661.9167 | 35 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.3 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 74.5333 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.5333 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 116.6 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1328 | 83 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16421.25 | 87 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 530.4 | 144 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7276.6331 | 419 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17584.8 | 816 | 1 | 1 | 0741-Boiler recirculation pumps - motors | SF-Startup Failure | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10312.4 | 812 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.3833 | 49 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.6 | 49 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.95 | 49 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1136 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6140 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.6 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.3333 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.5333 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.4166 | 85 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 164.8 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 213.7666 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14172.9357 | 236.15 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 418266.1166 | 299 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 38741.0999 | 261 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58180.8 | 816 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 370758.8 | 412 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.4 | 48 | 1 | 3 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.55 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.6 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78.3 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 260 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 272 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 889.6 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1073.25 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1152 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.0833 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.25 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.4333 | 61 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1373.5166 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6087.9 | 63 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.2 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.3333 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 951.4166 | 49 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1020.85 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1037.4 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.1666 | 50 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 253.3333 | 95 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 277.3666 | 53 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1428.3 | 81 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 402987.3832 | 319 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 79810.3 | 467 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 188.5 | 13 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 800-Miscellaneous
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 462 | 88 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 850-Combined Cycle Block
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1205 | 60 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55091.25 | 45 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1446.4999 | 330 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D2-Forced - Delayed | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18072.9 | 467 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 146.6666 | 160 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16796.433 | 467 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 745.2 | 138 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2071.8 | 108 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.0333 | 43 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D2-Forced - Delayed | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 20 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 584.97 | 27.9 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12441.1998 | 228 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | SF-Startup Failure | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3000.8333 | 130 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.7 | 3 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 472.75 | 155 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | SF-Startup Failure | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 4030 | 155 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 851-CC GT units
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1394.6329 | 602 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5632.1332 | 212 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9253.6332 | 361 | 1 | 1 | 0760-Boiler recirculation valves | U2-Forced - Delayed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5544.25 | 331 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 603.425 | 241.37 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.6666 | 236 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20387.0331 | 658 | 1 | 1 | 0760-Boiler recirculation valves | SF-Startup Failure | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45462.9998 | 660 | 1 | 1 | 0760-Boiler recirculation valves | U3-Forced - Postponed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 541.3665 | 298 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1315.8 | 258 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 7232.8666 | 308 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 72.3333 | 62 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 850-Combined Cycle Block
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 5.1133 | 76.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 38.1148 | 326.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 41.5616 | 226.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 48.5683 | 126.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1374.955 | 376.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2165.9165 | 395 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7129.9996 | 552 | 1 | 1 | 0770-Other boiler recirculation problems | U2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 426.9265 | 376.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1040 | 320 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 830.9165 | 295 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 882.45 | 159 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 14.7249 | 176.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 18.8916 | 226.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2412.4995 | 750 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2184.9999 | 228 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 27.67 | 276.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1192.8831 | 376.7 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 612.4995 | 750 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10587.4995 | 750 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16137.4995 | 750 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 69.175 | 276.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 82.0632 | 351.7 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 137.5833 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 227.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 904.8 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 143 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 162.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 760.5 | 39 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 156 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 182 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 341.25 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 390 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 491.8333 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 390 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 924.0833 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 163.5833 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 240.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 169 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 152.75 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 149.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 191.75 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 198.25 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 325 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 331.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 185.25 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 188.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 210.1667 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 229.0167 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 260 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 302.25 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 351 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 396.5 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 3263 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 174.4167 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 188.0667 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 208 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 230.75 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 342.3333 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 383.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 543.15 | 17 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 582.25 | 17 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5547.6665 | 187 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27783.9995 | 690 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 472.8202 | 17.33 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 508 | 30 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 581.7 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 666.3 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43078.9998 | 690 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 988 | 19 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 725.5 | 30 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 5024.8333 | 118 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 426.9 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12528.8 | 48 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 472.8 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 456 | 19 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3360 | 63 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31068.8 | 448 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42008.6 | 164 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1625 | 32.5 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 650-Fluidized Bed
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 21417.9 | 282 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 3163.16 | 60.83 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4429.9998 | 300 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 28045 | 71 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 2753.9233 | 147.4 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 3397.1 | 161 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1449.3333 | 80 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2774.475 | 148.5 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 1470.5 | 173 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 861-CoG GT units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | TRE | Summer | 2054.25 | 165 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 861-CoG GT units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 2964.75 | 177 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 861-CoG GT units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | TRE | Summer | 2032.8999 | 174 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 861-CoG GT units
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6424 | 55 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6766.56 | 140.97 | 1 | 1 | 0782-Headers and caps | D3-Forced - Postponed | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4653 | 517 | 1 | 1 | 0782-Headers and caps | D1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21935.0999 | 153 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4102.5 | 150 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 860 | Co-generator Block | SERC | Off-Peak | 300.2667 | 16 | 1 | 1 | 0782-Headers and caps | U2-Forced - Delayed | 860-Co-generator Block
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 42818 | 542 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 224.1667 | 5 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 201.0333 | 74 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 7380 | 246 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36053.3332 | 520 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3174.5333 | 116 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4684.9998 | 300 | 2 | 2 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6291.1332 | 442 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3697.5 | 170 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22881.1665 | 635 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 559.9896 | 579.3 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13066.6666 | 320 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3458.25 | 159 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2865.0333 | 74 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7867.3997 | 417 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 111.65 | 20.3 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1258.7498 | 285 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 4875 | 300 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3012.5332 | 316 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 89.8333 | 55 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 11133.8333 | 55 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 0.91663 | 55 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 2142.9333 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 337.5 | 27 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 498.75 | 105 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 958.5332 | 182 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115.15 | 47 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 14539.45 | 23 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2156.25 | 125 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 831.8332 | 155 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.5997 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 247.5 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 759.5 | 155 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2338.485 | 437.1 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57010.4997 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 577.9167 | 19 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112 | 28 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 271.6333 | 29 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 800 | 40 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25 | 25 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 116.6666 | 125 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 355.8333 | 175 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 708.75 | 135 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 7245.8332 | 125 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 690.3833 | 23 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 4327.45 | 23 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 554.9999 | 450 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1343.2497 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6828.8998 | 306 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.75 | 135 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 283.5 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 290.2497 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 23.4666 | 64 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 513.3998 | 453 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 634.3333 | 110 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6703.8333 | 145 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1173.3333 | 110 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1309.4999 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1850 | 370 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.6665 | 220 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 398.9498 | 303 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 742.4999 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 115.425 | 76.95 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1017.7166 | 227 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 319.4999 | 135 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 646 | 19 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1010.5665 | 497 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1182.2305 | 466.67 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9048.9665 | 638 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1289.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4872.9998 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 430.6665 | 380 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 732.3497 | 453 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 891.25 | 93 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 70 | 40 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 852.5 | 110 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1625 | 125 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1928.6665 | 440 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2286.1665 | 638 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1295.8497 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 760.4998 | 270 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1185 | 300 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 910.5 | 18 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 410.4167 | 25 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 450 | 75 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 568.75 | 75 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175.4999 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 264.9999 | 300 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 504.9999 | 300 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1152.7497 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1292 | 340 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 66386.25 | 675 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.25 | 13 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 237.5 | 95 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 823.75 | 75 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 398.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 852.4999 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 57.75 | 45 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14741.8333 | 187 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2641.4999 | 135 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1348.6664 | 340 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2000.6997 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 189.9999 | 300 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 606.671 | 466.67 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1935 | 90 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 856.8 | 112 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 763.3333 | 25 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 22492.6 | 106.6 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1836.0833 | 55 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 11180 | 260 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D3-Forced - Postponed | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 33.7333 | 88 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 1850.2458 | 60.83 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 51.95 | 41.56 | 2 | 2 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 244.412 | 168.56 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 228.8899 | 292.2 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 860 | Co-generator Block | NPCC | Summer | 1230.255 | 210.3 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6795.4333 | 236.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 129.9733 | 243.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 317.3165 | 241 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 149.5 | 230 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 4001.55 | 309 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 100.7 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 993.3 | 92.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 244.8999 | 237 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 5288.4 | 108.48 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4038.6 | 318 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 63.25 | 253 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 143.6832 | 233 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 6313.1331 | 281 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 301.25 | 241 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4004.1665 | 310 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 600 | 375 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 70.2666 | 62 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 550.25 | 355 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 6400 | 256 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 30.6666 | 92 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1320.9165 | 605 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 878.275 | 92.45 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 395.3115 | 73.89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 214.2 | 153 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Winter | 29.3333 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 87.4999 | 150 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 111.9 | 149.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | NPCC | Winter | 4457.3999 | 171 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 14.1666 | 170 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 88 | 55 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Summer | 27.1333 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | NPCC | Winter | 2154.6 | 171 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 13.895 | 39.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 413.784 | 73.89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 3316.1333 | 154 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 132 | 176 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 83.05 | 151 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 10.0666 | 151 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Summer | 28.6 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 528.8332 | 167 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 154.5833 | 175 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 233.275 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 2227.25 | 151 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 344.1665 | 175 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | NPCC | Winter | 68.6166 | 179 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 318.2933 | 149.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 18.5266 | 39.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | NPCC | Winter | 2607.75 | 171 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 3242.6999 | 162 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1901.5833 | 95 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 16.16 | 48.48 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 23.615 | 47.23 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 54.2135 | 98.57 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 262.4175 | 49.05 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 149.296 | 29.76 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 274.68 | 49.05 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 80.3833 | 91 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 375.6332 | 191 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2956.7999 | 126 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 646.7332 | 218 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 360 | 90 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1886.5 | 98 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 59.5 | 102 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 21.92 | 109.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 1575 | 125 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 41.1665 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 4283.3332 | 250 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 188.3833 | 89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 24.12 | 60.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | TRE | Summer | 874.5 | 165 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | TRE | Summer | 135.2 | 78 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 862 | CoG steam units | SERC | Winter | 1165.0833 | 31 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 10019.3332 | 280 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 132.473 | 120.43 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 284 | 60 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 682.7332 | 532 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 126.5832 | 245 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 802.4 | 472 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 244.8999 | 237 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 2038.5 | 270 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 450.7565 | 186.52 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 31.5 | 70 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 11.5 | 138 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 32.55 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Summer | 118.02 | 168.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 88.0833 | 151 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 418.6 | 182 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 82.5 | 150 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 103.8333 | 70 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 698.65 | 157 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 467.6 | 167 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Winter | 7136.3999 | 171 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 47.8333 | 70 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 120.1666 | 70 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 309.3333 | 160 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 90.4166 | 155 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 442.4 | 158 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 57.4991 | 98.57 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 1042.25 | 379 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 104.6491 | 70.55 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 158.5333 | 82 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 86.3332 | 185 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 32.88 | 109.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 218.7616 | 110.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Winter | 218.5 | 95 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 20.832 | 29.76 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 18.2666 | 109.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 113.3666 | 179 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 263.925 | 117.3 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 231 | 462 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1175 | 125 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 235 | 235 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 136.8 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 103.8333 | 70 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 0 | 0 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1128.1666 | 70 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1408.75 | 175 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 80.478 | 134.13 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 207.6666 | 70 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 98.15 | 151 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 213.5 | 70 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 104.6491 | 70.55 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 64.0705 | 98.57 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 147.1999 | 138 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 28.5 | 190 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 34.8333 | 190 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 65.6666 | 197 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 478.3999 | 138 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 238.9165 | 235 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Summer | 5.8008 | 69.61 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65327.7 | 47.1 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26293.5998 | 552 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0814 | In-bed bubble caps (FBC only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 538.9583 | 32.5 | 1 | 1 | 0814-In-bed bubble caps (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 72048 | 228 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 105991.4999 | 171 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5465.9833 | 41 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13730.3332 | 340 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3540 | 30 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 985.2267 | 18.2 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3460 | 10 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20426.9997 | 495 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44539.5 | 230 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11415.9998 | 240 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72225.9991 | 1320 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 72912.5999 | 108 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 30360 | 220 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6450.73 | 16.9 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160 | 5 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 21794 | 51 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 27896.1499 | 111 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5950.62 | 15.6 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 584.25 | 9.5 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1489.6 | 5.6 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 27500.7333 | 44 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2044.4664 | 364 | 1 | 1 | 0820-Casing | SF-Startup Failure | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 102960 | 520 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 48972.5665 | 181 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1020 | 40 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 22800 | 114 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1377.85 | 51 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14736.1 | 46 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 128416.6666 | 230 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.6933 | 2.2 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4240.2967 | 18.2 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 275889.6 | 414 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.9575 | 0.13 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97 | 9.7 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 109.2667 | 11 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 20640.7667 | 41 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 4330.9 | 161 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4809.35 | 18.2 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 19890.3998 | 552 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 126702.3996 | 528 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 888.7 | 6 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 226.8375 | 39.45 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12429.7617 | 17.3 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 79101.2998 | 738 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 17351.4 | 239 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1854.4726 | 137.03 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 3055.5 | 126 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 852-CC steam units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 5103 | 126 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.6333 | 71 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 704.7833 | 49 | 1 | 1 | 0830-Doors | D2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2745.8333 | 250 | 1 | 1 | 0830-Doors | SF-Startup Failure | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 462.8666 | 131 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.85 | 61 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 326.6667 | 20 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56346.9994 | 870 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219.65 | 191 | 1 | 1 | 0830-Doors | U3-Forced - Postponed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 315.169 | 137.03 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 995.1333 | 46 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4155.775 | 24.7 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 221 | 130 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 852.4999 | 165 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 1828.3196 | 527.4 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 650-Fluidized Bed
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2686.9669 | 159.78 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | MRO | Summer | 1848 | 154 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 973 | 139 | 1 | 1 | 0830-Doors | SF-Startup Failure | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | MRO | Summer | 10972.5 | 55 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2784.8399 | 165.6 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | MRO | Summer | 1356 | 113 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | WECC | Off-Peak | 3631.4499 | 177 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | WECC | Off-Peak | 184 | 23 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 2400.4499 | 117 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 862-CoG steam units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.16 | 168.6 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1778.6666 | 115 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14688 | 102 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 411 | 3 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 860.9867 | 16.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29250 | 195 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35528.0833 | 193 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38554.9665 | 193 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.27 | 90.9 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.2466 | 103.6 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 292.9 | 2.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1817.2 | 30.8 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3899.7 | 27 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2921.5999 | 192 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46857.1833 | 193 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60179.1999 | 192 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.5133 | 50.8 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 109575 | 150 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1362.9 | 118 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2389.6 | 412 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7152.66 | 15.8 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 303.2 | 37.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1344.84 | 12.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75292.7499 | 195 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.5066 | 70.4 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5121.18 | 27.6 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 68904 | 132 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 95940 | 82 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 9950.9333 | 64 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76 | 19 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2721.65 | 29 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7390.8333 | 175 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46220.2833 | 193 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12273.3332 | 200 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300.3 | 30.8 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1120 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81 | 3 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6665.7066 | 83.2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 726.56 | 15.2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1647.03 | 21.7 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1776.2 | 21.4 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 329.46 | 64.6 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3505.275 | 13.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55233.3833 | 193 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 52913.6665 | 220 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5134.9998 | 300 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9360 | 195 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14568.2833 | 193 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44544 | 192 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2015 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 8229.6233 | 74.6 | 1 | 1 | 0840-Refractory and insulation | U3-Forced - Postponed | 650-Fluidized Bed
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 822.15 | 63 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5947.5 | 130 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 747.5 | 130 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38489.7497 | 507 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 533.375 | 42.5 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 54.4 | 32 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 13243.6 | 293 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | MRO | Winter | 26586.4666 | 161 | 1 | 1 | 0847-Other expansion joints | U2-Forced - Delayed | 851-CC GT units
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 52.5666 | 166 | 1 | 1 | 0847-Other expansion joints | SF-Startup Failure | 851-CC GT units
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | MRO | Winter | 27319.0166 | 161 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 851-CC GT units
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 16713.4333 | 166 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 851-CC GT units
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 319.6666 | 70 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 852-CC steam units
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 23116.3332 | 140 | 1 | 1 | 0847-Other expansion joints | U2-Forced - Delayed | 852-CC steam units
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Gas | GG | 861 | CoG GT units | WECC | Winter | 5155.5919 | 267.36 | 1 | 1 | 0847-Other expansion joints | D2-Forced - Delayed | 861-CoG GT units
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Gas | GG | 861 | CoG GT units | WECC | Winter | 5988.864 | 267.36 | 1 | 1 | 0847-Other expansion joints | D2-Forced - Delayed | 861-CoG GT units
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 861 | CoG GT units | SERC | Winter | 11575 | 50 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 861-CoG GT units
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2015 | Gas | GG | 861 | CoG GT units | SERC | Summer | 6516.25 | 65 | 1 | 1 | 0847-Other expansion joints | U3-Forced - Postponed | 861-CoG GT units
0848 | Inlet panel | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 6612.5332 | 137 | 1 | 1 | 0848-Inlet panel | U2-Forced - Delayed | 851-CC GT units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 481.4667 | 23 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 180.7 | 39 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 11.655 | 33.3 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5228.3 | 67.9 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 1188.55 | 33 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 977.9 | 33 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 2877.25 | 51 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 37.4583 | 2.5 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 218.2267 | 10.4 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 3513.4 | 33 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 712 | 89 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16690.9167 | 13 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 3.8783 | 1.3 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 1186.7833 | 31 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16653.1107 | 261.91 | 1 | 1 | 0850-Other internal or structural problems | U2-Forced - Delayed | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 28583.4031 | 337.4 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 650-Fluidized Bed
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 953.7496 | 525 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 650-Fluidized Bed
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 790.4666 | 71 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 850-Combined Cycle Block
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Winter | 182833.5833 | 35 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 9310.8 | 6 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2965.9333 | 17 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 14583.45 | 7 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 209.05 | 37 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 426.5333 | 56 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 364.5 | 45 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 251.5 | 5.03 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 146.1832 | 179 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16164.3999 | 168 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | NPCC | Summer | 13635.6349 | 173.85 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 88.4 | 31.2 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 189 | 28 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 190.6666 | 65 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 328.0666 | 133 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2319.1665 | 605 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4775.3331 | 380 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 800.3333 | 20 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 31.1667 | 22 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2116 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 638.4666 | 122 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2715.6 | 248 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57324 | 240 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1018.4 | 48 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1833.4333 | 13 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 310.5 | 54 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 983.3333 | 50 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 513.3333 | 20 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 800-Miscellaneous
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 2137.2 | 78 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 139.1866 | 189.8 | 1 | 1 | 0857-IP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 113.7865 | 200.8 | 1 | 1 | 0857-IP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30503.9999 | 180 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7148.9 | 426.8 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3389.4 | 84 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54.6667 | 16 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 11232 | 144 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5691.1517 | 45.59 | 1 | 1 | 0859-Tube external fins/membranes A | U2-Forced - Delayed | 100-Fossil-Steam
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 40302.75 | 255 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 850-Combined Cycle Block
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56 | 42 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.1 | 33 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.7 | 6 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 515.8833 | 13 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 664.6999 | 102 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.6666 | 55 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 265.1 | 11 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0 | 0 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1361.1093 | 46.72 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24.2 | 22 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.1333 | 52 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 271.35 | 81 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 224.2 | 12 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 361.3333 | 20 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168.2667 | 8 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2994.8786 | 50.32 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.9166 | 85 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 576.5968 | 9.91 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 698.2 | 12 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.91 | 2.1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.65 | 27 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1058.65 | 93 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2285.2932 | 339.4 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 275.6177 | 136.67 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 293.75 | 125 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.11667 | 0.2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 241.5563 | 64.13 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1149.9996 | 600 | 1 | 1 | 0870-Soot blowers - steam | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 324 | 81 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14704.1 | 71 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.25 | 0.25 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2629.75 | 157 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.6333 | 19 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1103.6 | 248 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.4999 | 129 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1150 | 100 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28173.8333 | 217 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4443.3332 | 200 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.73667 | 1.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 90.1333 | 52 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1149.1999 | 312 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.75 | 3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.44 | 55.2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 984.5833 | 139 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.13 | 34.13 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 59.1666 | 50 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.6666 | 130 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 426.6666 | 200 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 539.4666 | 56 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.5225 | 1.65 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28685.3332 | 496 | 1 | 1 | 0870-Soot blowers - steam | U1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48854.6665 | 440 | 1 | 1 | 0870-Soot blowers - steam | U2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.775 | 1.5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1363.8332 | 167 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2560.25 | 77 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.375 | 0.5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0871 | Soot blowers - sonic | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 344 | 32 | 1 | 1 | 0871-Soot blowers - sonic | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 511.595 | 32.9 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 875.7667 | 47 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1412.1232 | 259.9 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.8333 | 50 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129.85 | 49 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48.8167 | 29 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11208.2667 | 22 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4.3166 | 37 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 389.7331 | 296 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6013.15 | 319 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50 | 100 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84 | 35 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 118.75 | 75 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 86.4 | 72 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 223.1666 | 103 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3670.3331 | 308 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 488.0333 | 22 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 179.4 | 78 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 228.15 | 117 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2272.4667 | 17.8 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 979.6 | 316 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 450 | 100 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115 | 115 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 581.7166 | 167 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2812.5 | 125 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 5.11 | 5.11 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1790.24 | 10.72 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 12 | 8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 94.1803 | 15.61 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 874.2 | 36 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114.8332 | 265 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D3-Forced - Postponed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1618.3333 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 747.6333 | 22 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12732 | 240 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2102.0833 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2633.9999 | 180 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8229.1666 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 854.25 | 255 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1206.5 | 30 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 44.7333 | 22 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 53.25 | 12.78 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14578.4332 | 301 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D3-Forced - Postponed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4783.3332 | 200 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 215.88 | 35.98 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 916.6666 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.5833 | 49 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 471.7333 | 244 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11656.25 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.6666 | 160 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2112.55 | 167 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 26.51 | 7.23 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 324.3333 | 35 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 308.9666 | 31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 49.536 | 10.32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 49.8333 | 23 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 389.3333 | 20 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 710.6666 | 130 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1200 | 250 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1824.6666 | 170 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2538.75 | 75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5400 | 300 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 394.6666 | 40 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2447.4999 | 165 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 110.8333 | 19 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 178.25 | 31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 166.95 | 53 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 12939 | 227 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1275 | 36 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.9333 | 8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360 | 15 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1075 | 215 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 514 | 60 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 10.74 | 7.16 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 75.25 | 21 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 12.125 | 4.85 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 41.6 | 8.32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 56.7957 | 14.14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2369.0332 | 143 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1357.5 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 90 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2119.3332 | 170 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1927.7 | 74 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 20.68 | 5.17 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 300.8333 | 25 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 308.9666 | 31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2752.8665 | 238 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 261.9 | 18 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2292.15 | 111 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5162.5 | 295 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 8.9167 | 4.28 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 24 | 12 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 22.968 | 7.83 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 25.6667 | 22 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 66.1333 | 16 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 269.7 | 31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 740 | 37 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 137808 | 1320 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 673.8666 | 152 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25 | 75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.2999 | 171 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 217.0333 | 34 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2220.1 | 149 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7336.4332 | 194 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.5 | 3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72.3332 | 140 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10317.3332 | 265 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 4 | 4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 554.0475 | 23.83 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 13 | 12 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 94.5 | 21 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2307.5 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | NPCC | Off-Peak | 5208 | 37.2 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 115.5 | 55 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | SERC | Summer | 3999.6 | 66 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 168.045 | 15.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126.9333 | 56 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.3333 | 80 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D3-Forced - Postponed | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 214.1666 | 257 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.3332 | 140 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23177 | 140 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1947.5 | 19 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2226 | 212 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1626.1 | 322 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1625.25 | 165 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 358.2 | 27 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520 | 26 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2633.49 | 90.81 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D2-Forced - Delayed | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198353.3663 | 577 | 1 | 1 | 0885-Fly ash Removal System - wet transport | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.301 | 5.13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.4313 | 1.13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.9483 | 15.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180.2458 | 45.25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 438.97 | 62.71 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 794.04 | 66.17 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 495 | 33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 289.9999 | 120 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4237.15 | 49.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2199.9998 | 330 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1128.9931 | 340.4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1228.5 | 90 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 544.147 | 7.89 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1870.95 | 124.73 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1442 | 180.25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2983.79 | 129.73 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 384 | 64 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 502.02 | 83.67 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 73.78 | 20.4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 612 | 153 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 739.35 | 159 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2897.5 | 190 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5716.6665 | 250 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2796 | 240 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5261.1 | 175.37 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 457.98 | 76.33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 413.695 | 47.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1000.9999 | 231 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3407.8665 | 244 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.5 | 98 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 260.8 | 32.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 192 | 96 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 166.98 | 27.83 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 345.96 | 12.4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31596.0831 | 335 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.1667 | 7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 214.5 | 16.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 632.4 | 136 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1777.4999 | 270 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2180.8 | 94 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.5767 | 13.4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 483.66 | 53.74 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 674.56 | 84.32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 695.01 | 231.67 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 918 | 76.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1111.98 | 185.33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1958 | 244.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 308 | 44 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 869 | 86.9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 135.8 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 4879.9166 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98.49 | 14.07 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 962.9998 | 270 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4489.6 | 244 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.4 | 4.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 292.2667 | 16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 879.6666 | 70 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2544 | 159 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2770 | 120 | 2 | 2 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3539.1666 | 155 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112 | 112 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 255 | 63.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1698.97 | 242.71 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 48.9 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.0557 | 14.23 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 722.9999 | 180 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 93 | 93 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2107.08 | 117.06 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 255.5 | 36.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1045 | 95 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 670.11 | 95.73 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 8.1633 | 7.9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 232.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 530.3333 | 148 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1382.9999 | 180 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1036 | 259 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12001.16 | 157.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 543.69 | 60.41 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6626.25 | 116.25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72769.9998 | 600 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 415 | 83 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 73.5 | 10.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 309.3333 | 58 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 173.3333 | 32.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 768.2665 | 268 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 97.1633 | 10.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 97.5 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 400.9 | 21.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 304.695 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 630 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 722.3 | 23.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 117 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 169 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 88.4 | 22.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 102.2 | 7.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 154.7 | 22.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 56.575 | 7.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 563.0833 | 23.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 110.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 143 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 275.1667 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1514.5 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 100.8 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 153.9 | 17.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 3859.7867 | 29.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 335.1417 | 13.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 16.5 | 3.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 598 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 659.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 135.6 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 147.8417 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 35.955 | 14.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 76.4 | 19.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 156 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 245.66 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 134.85 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 252.845 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 81.305 | 16.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 188.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 289.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 680 | 17 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1480 | 37 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 146.6 | 6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 488.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 480.5 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1858.4999 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 164.6666 | 95 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1232.9998 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 416.5093 | 59.36 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1498.7499 | 165 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 58.5833 | 95 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 665.26 | 44.4 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14778.1665 | 530 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 616.85 | 73 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31785 | 815 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 487.6666 | 154 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1229.6665 | 217 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 420.75 | 165 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35942.3166 | 77 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 165757.5 | 530 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 55949.75 | 815 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4700 | 200 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 244.9499 | 207 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 107.6666 | 95 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 147.4833 | 88.49 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1500.2665 | 464 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4950 | 750 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 49.6 | 9.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 189.5167 | 8.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 367.425 | 21.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1338.6 | 194 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4652.7666 | 194 | 1 | 3 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 284.9999 | 180 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 855.5 | 295 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1853.2166 | 251 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3195 | 213 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 518 | 64.75 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 566.8332 | 179 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25536 | 320 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.85 | 167 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119.6332 | 194 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2460.3 | 139 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 99 | 12 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 423.6 | 12 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1280 | 40 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4964.7999 | 96 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1049.0666 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2672.01 | 296.89 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3418.95 | 148.65 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 116.2 | 58.1 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1933.5332 | 194 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3184.8332 | 194 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1084.4998 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1075.2 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5372.2666 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2202 | 275.25 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2631.96 | 292.44 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 488.3686 | 145.06 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.3 | 56.3 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41574 | 507 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 386.9999 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 490.4998 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 307.4999 | 90 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 29.75 | 15 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6857.0665 | 416 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 765.4166 | 167 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340 | 80 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1005.7 | 178 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1480.4999 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3765 | 251 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 304.99 | 43.57 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 127.6 | 24 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1313.2 | 46.9 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.2499 | 87 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1385.9999 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1530 | 170 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1746 | 194 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 777.75 | 255 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 805.2 | 244 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 27.5 | 10 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 628 | 120 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1579.5 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1967.1664 | 370 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2214.9167 | 35 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5199.6665 | 190 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2292.4332 | 194 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4652.7666 | 194 | 1 | 3 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2533.8667 | 32 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1108.5667 | 14 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5482.75 | 455 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 186 | 120 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1924.7733 | 81.1 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3780 | 315 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80547.9995 | 780 | 1 | 1 | 0893-Bottom ash water pumps and motors | U3-Forced - Postponed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4550 | 455 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 490 | 84 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3776.8332 | 310 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4880.25 | 405 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3226.6 | 442 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 592 | 120 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9703.6666 | 172 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4436.1 | 164.3 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1327 | 265.4 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2757.2 | 244 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 419 | 209.5 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440.65 | 21 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 832.4999 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1138.4998 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 204.792 | 59.36 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1464 | 244 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4788.2999 | 198 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1482 | 148.2 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116754 | 870 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2435.9333 | 244 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160 | 160 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 153.99 | 51.33 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 464 | 116 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 460.95 | 21 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 860 | 172 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2435.9333 | 244 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52195.3332 | 472 | 1 | 1 | 0894-Bottom ash piping and valves | SF-Startup Failure | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 11.5 | 11.5 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 650-Fluidized Bed
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 123.83 | 18.3 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 800-Miscellaneous
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1264.6167 | 23 | 1 | 1 | 0894-Bottom ash piping and valves | D3-Forced - Postponed | 800-Miscellaneous
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 734.9999 | 180 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 32.95 | 3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 45.375 | 4.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 186.4 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 243 | 13.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 62.675 | 11.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 164 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 556.1832 | 221 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 724.5332 | 152 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38670.2331 | 766 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3414.2999 | 171 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 34 | 4 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 125 | 25 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 251.6967 | 13.4 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1379.4 | 24.2 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2881.0665 | 292 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1549.7332 | 236 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5753.5998 | 372 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 54906.6664 | 800 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 137.5 | 10 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 592 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 112 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 427.8 | 24.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.15 | 221 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6861.9996 | 564 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 968.9999 | 342 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1029 | 196 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5360.6664 | 430 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 11847.5906 | 570.51 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 95.5833 | 15.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 183.75 | 24.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 264 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 201 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 169.5833 | 55 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 455.2166 | 143 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1434.9999 | 210 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 22831.8664 | 436 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 2244.75 | 45 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 125.7332 | 328 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2722.4998 | 297 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2784.1666 | 257 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 99.9 | 18 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 152 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 179.55 | 27 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 23.4 | 9 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 200 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 244 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.1 | 221 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2425.2999 | 237 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39451.9994 | 840 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 38 | 30 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23634 | 390 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1394.125 | 293.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 131.1 | 11.4 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 285.8 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 438.75 | 15 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 26.25 | 15 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2111.1665 | 265 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 728 | 182 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63253.5995 | 816 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1236.4 | 281 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 20.5 | 6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 202.1 | 25.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 618 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 132.75 | 27 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84 | 40 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 372.3 | 438 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1170.35 | 263 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 18.6 | 18 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 159.3 | 27 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 559.6 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 214.8883 | 16.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 56.5 | 22.6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 672.8333 | 22 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 864.475 | 22.9 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 55 | 11 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 174.6 | 27 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86.7 | 102 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 616.6665 | 250 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 624 | 156 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1189.1 | 253 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3412.1331 | 326 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | TRE | Winter | 524.05 | 47 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18806.2496 | 531 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | SERC | Summer | 1410.2 | 66 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 120.5 | 24.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 290.4 | 12.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 197.4 | 14.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | SERC | Winter | 1216.6 | 66 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2013.6666 | 28 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4335.4998 | 690 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | U1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1234.1333 | 89 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 27.04 | 31.2 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 351.05 | 119 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253 | 60 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16913.3329 | 590 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 28.5333 | 16 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135.5333 | 19 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332.1833 | 19 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 494 | 39 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5449.5999 | 96 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14270.4 | 96 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51885.2664 | 659 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 35 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5659.5 | 210 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 545.5166 | 71 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 496.6666 | 40 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28786.3332 | 511 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3597.9999 | 210 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17714.6663 | 511 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47392.8 | 364 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1347.3332 | 215 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1560.65 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 614.25 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1008.5833 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 4836 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 682.5 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 573.3 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 383.5 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 611 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2934.75 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 400 | 80 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 176 | 80 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.5 | 30 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 507.7332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 519.5666 | 218 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 990 | 330 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1838.8333 | 85 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2366.9998 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55.4999 | 90 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.3333 | 52 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.75 | 33 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1029.1665 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4652.7666 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5851.9333 | 244 | 1 | 7 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.25 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 224.1999 | 177 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 248.4332 | 257 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 571.6666 | 140 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 638.4 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 672 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30 | 36 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 35.8333 | 43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 144 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 12 | 1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.678 | 51.13 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34.4749 | 82.74 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.8975 | 50.07 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.5806 | 75.22 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 656.3666 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2300.6664 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 265.44 | 47.4 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1920.8 | 48 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 661.6666 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5372.2666 | 224 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.6 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 164.7 | 27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 768.4 | 102 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 900 | 180 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1768.5 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3342.8 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4080.4666 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 337.5 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 380.2666 | 124 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 537.5 | 150 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 668 | 167 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 185.217 | 51.93 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.5023 | 139.66 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 40.11 | 19.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 8 | 1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 10 | 1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 34 | 1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 48 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.526 | 78.42 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.027 | 73.71 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.3375 | 70.41 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 108.048 | 90.04 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.271 | 56.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 900.6 | 114 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 311.9664 | 382 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 423 | 180 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 645.8666 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2464 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 365 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 416.25 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 457.2 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14446.6665 | 440 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1709.0196 | 236.27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 14.1867 | 13.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 306 | 17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4 | 2 | 1 | 3 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 136 | 17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 180 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26 | 52 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32.9499 | 79.08 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.5267 | 49.58 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.9 | 63.48 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.0666 | 91 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55245 | 580 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 741.0666 | 112 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3647.4666 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.6666 | 140 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 195 | 65 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 357.5 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 877.5 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18.6 | 12.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 79.66 | 8.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 361.395 | 240.93 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 47.9733 | 25.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 19.3333 | 11.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 503.5 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 104.4367 | 32.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 668 | 167 | 1 | 3 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.0655 | 67.29 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.1865 | 63.39 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.9366 | 101.81 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1463 | 133 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 169.05 | 49 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7368 | 307 | 1 | 1 | 0920-Other slag and ash removal problems A | SF-Startup Failure | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.3333 | 40 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189 | 90 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 668 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 660.8 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2310.9332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30.13 | 30.13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162.5 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 366.5 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1394 | 139.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 80.5533 | 28.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 10 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 38 | 1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 72 | 3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.242 | 74.14 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138.992 | 99.28 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 906.3 | 114 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.9723 | 54.47 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.2586 | 51.11 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.2118 | 76.99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 248 | 124 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 544.9333 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 880 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1020.5331 | 344 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3488.7666 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5372.2666 | 224 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2160 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 451.486 | 56.91 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2247 | 187.25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 40.5067 | 24.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 78.4 | 22.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 45 | 3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 195 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.111 | 77.46 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.8933 | 59.68 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.9341 | 77.03 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 503.1 | 234 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 84 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 382.2 | 7.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 897.6 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1736 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2688 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3542.9332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 193.3333 | 80 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 76.8998 | 98.17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1042 | 260.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 54.1666 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 108.8 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 77.42 | 15.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 160 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 243.1 | 34 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 16 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 140 | 14 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.227 | 44.94 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.905 | 85.81 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.575 | 91.15 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2904.7499 | 135 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5987.5 | 479 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20.725 | 82.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.6 | 52 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.29 | 69.87 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.728 | 51.99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4 | 1 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 804.3832 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1402.1665 | 235 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1982.4 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2204.9998 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2524.6666 | 140 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.75 | 7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5005.2 | 344 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5721.8 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.0667 | 32 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.6667 | 35 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186.6666 | 80 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 986.25 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 994.5 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1120 | 280 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 64.4 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 20.328 | 9.24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 108 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 270 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 45 | 9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20.075 | 48.18 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.19 | 60.38 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.1266 | 88.69 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.2333 | 66.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33.108 | 82.77 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 1629.432 | 59.36 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2161.6667 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 328.5333 | 88 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 46.6666 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 80279.7098 | 625.8 | 1 | 1 | 0920-Other slag and ash removal problems A | U3-Forced - Postponed | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 119.8 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 743.2833 | 23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1069.25 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 16.9 | 6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 120 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 506.7883 | 12.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 581.515 | 29.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 251 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 364.3333 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 373.3333 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 913 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 2586.1 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 3472.7 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1832.5166 | 43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 58.9 | 9.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 157.325 | 9.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 185.5 | 14 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 42.56 | 11.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 99.7 | 6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 103.6667 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 320.95 | 21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 575.6 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 16272.3 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Other | BM | 800 | Miscellaneous | SERC | Winter | 81991.8 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 104.4 | 26.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 139.15 | 12.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 82.5 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 3204.2332 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 3362.6666 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 30167 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 11271.4 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 11678.8 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 2961.0866 | 96.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 3232.4133 | 117.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U2 | Forced - Delayed | 2015 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 4219.2 | 293 | 1 | 1 | 0930-Bed material coolers | U2-Forced - Delayed | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 160 | 40 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 1290.96 | 107.58 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 39.5 | 47.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 391.04 | 62.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 190.96 | 23.87 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 2147.22 | 47.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 273.84 | 50.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 2519.5733 | 126.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 2200 | 100 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1102 | 110.2 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 2682.12 | 82.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 226.72 | 62.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 245.69 | 47.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 39 | 39 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12025 | 325 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 378.6666 | 320 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 27770.08 | 351.52 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2792.96 | 349.12 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 5525 | 325 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 4314.24 | 342.4 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0932 | Bed material transport tanks/hoppers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 3084.9132 | 129.8 | 1 | 1 | 0932-Bed material transport tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 7389.36 | 118.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 2624.7999 | 115.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 723.35 | 125.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 364.4333 | 58 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 378 | 126 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1221.3333 | 80 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2015 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 7129.6666 | 293 | 1 | 1 | 0936-Bed material conveyors B | U1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 582.75 | 185 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 88.4 | 104 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 232.5 | 150 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 783.0333 | 169 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2530.1666 | 170 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 3433.6 | 74 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 58.75 | 75 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 904.1666 | 155 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2305.5 | 145 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2926.5833 | 145 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 233.0666 | 87.4 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D2 | Forced - Delayed | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 5908 | 280 | 1 | 1 | 0950-Other bed material system problems | D2-Forced - Delayed | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 164.5 | 35 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 291.6666 | 125 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 590.8333 | 50 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1049.9998 | 225 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 487.9999 | 183 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 297.9166 | 125 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 300 | 150 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 344.75 | 105 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 704.45 | 73 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 936.8333 | 73 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 423.7499 | 225 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2015 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 944.1333 | 73 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 108.9 | 12.1 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 361.1 | 15.7 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 38018.7166 | 227 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 488 | 24.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 18.8 | 18.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 869.2 | 21.2 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 91.2 | 72 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 380 | 9.5 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 59427.3866 | 337.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 1811.3708 | 37.75 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 3830.1666 | 335 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 23729.8664 | 335.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 590.4 | 24.6 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 6.4167 | 11 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 26.25 | 21 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2015 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 3217.5 | 54 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2015 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 18417.6 | 288 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 850-Combined Cycle Block
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 3490.4333 | 49 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 851-CC GT units
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2015 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 2477.75 | 51 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 860-Co-generator Block
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 455 | 140 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 275.8 | 21 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.25 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 736 | 92 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 742 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1218.75 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2214.6666 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2446 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1100.6666 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2174.2 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 3.905 | 21.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 552 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 13 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 17.5867 | 0.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 500.25 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 2164.1433 | 27.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1188.3 | 23.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1382 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3976.4999 | 99 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 859.5 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2964 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3670.7666 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3780 | 168 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4620 | 220 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9371.9999 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11384.8328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13871.0832 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15343 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16975.6665 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32798.0332 | 259 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35420.5998 | 372 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37327.5 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 39347.3327 | 241.37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59953.6664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68428.5 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 137769.3328 | 812 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4092 | 176 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5294.7333 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7186.4998 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9102.5 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10508.75 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12985.5332 | 218 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15829.6666 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16460.4 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17065.1666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18070.3999 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20223 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35569.3328 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37999.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50989.6664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51550.95 | 471 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60362.1332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91578.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 251.25 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4251 | 117 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4627.0832 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12128.9998 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14407.35 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15962.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24612.2665 | 265.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27302.9665 | 554 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27844.65 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32458.6664 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43166.4 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50093.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101397.9991 | 1320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108204.5 | 758 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 146137.5 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 8322.75 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4087.2 | 52.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 20681.4066 | 338.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 37976.4662 | 754 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 11513.3333 | 220 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 22005.321 | 434.03 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 31148.2999 | 402 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 42614.512 | 434.03 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 51445.6997 | 453 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1093.35 | 37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3837.6666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9943.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14872 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34042.95 | 453 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12044.9998 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71891.3 | 442 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22223.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24137.6331 | 658 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65306.5 | 658 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 17421.9829 | 641.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16596.7998 | 565.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 20719.5997 | 831 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 58879.2495 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2902.2499 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4227.4999 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22040 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11457.6 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44548.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.3 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2535.85 | 41 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.4 | 48 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 271.9665 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2498.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 467.5 | 11 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 566.4 | 23.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 949.5 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 20.8112 | 14.03 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 38300.6332 | 137 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 255.4665 | 479 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4913.9999 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2909.3333 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3591.4999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3606.8331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4566.6 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5063.3333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5515.5331 | 742 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9032.1 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 12140.911 | 241.37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12701.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14658.5999 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16146.6666 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22862.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23508.8833 | 181 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24753.6 | 382 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27274.75 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57408.3328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 73519.833 | 530 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83573.9331 | 742 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4075.4999 | 99 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8316 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 8871.1996 | 238.58 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13200.9331 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13824 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15686.5 | 229 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24576 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29847.6665 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76077.45 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92309.9998 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2365.7 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4754.6333 | 98 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5887.6666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6782.3999 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7225.2 | 223 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8148.9999 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8649.8665 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10653.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11212 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12101.4366 | 65.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12524 | 505 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16029.5833 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22315.3333 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24249.4999 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25243.2498 | 555 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 27216.8009 | 598.61 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40652.6664 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53160.9331 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 60803.7329 | 659 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63570 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79591.95 | 783 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105613.6497 | 783 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34225.5331 | 598 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8124.0997 | 411 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 10089.0166 | 113 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 17388.7998 | 528 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 20953.7 | 317 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36858.2665 | 404 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 73317.5997 | 432 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2364 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3036 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 22761.3 | 102 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | RFC | Winter | 49498.3331 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 20008.783 | 434.03 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7701 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15585.3665 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19167.1332 | 354.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20663.5 | 442 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64653.5829 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124901.4 | 871 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22489.5833 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27980.7 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40698.7332 | 412 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71825 | 442 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5825.05 | 187 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35279.95 | 839 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8221.8 | 137.03 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38192 | 440 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38828.7999 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4826.9666 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77 | 77 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 244.2 | 407 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 467.5 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1097.5 | 43.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340.9999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.33333 | 0.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.375 | 0.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.25 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104 | 8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 154.1333 | 2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 281.05 | 77 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 657.4167 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1248.75 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 298 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 421.9733 | 12.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 672 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1967.73 | 367.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1428 | 7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2050 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18159.05 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 38454 | 754 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.8733 | 52.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2103.5 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4409.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7973.4166 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9486 | 372 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9954 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12998.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13973.1666 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15885 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15992.5163 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 16232.697 | 242.46 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20916 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21517.75 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23281.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23362.7332 | 364 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23957.633 | 446 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27452.7 | 423 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35441 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40224.1166 | 197 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48391.0663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56037.3331 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61440.8331 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61483.3331 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65412.5663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6720 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7895.9199 | 129.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9823 | 220 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10605.1666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13030.7165 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 15300.9306 | 238.58 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 15925.215 | 238.58 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16791.25 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18832.9166 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22064.3499 | 363 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22549.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25647.65 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29357.6666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37104 | 773 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50554 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55622.9665 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62474.4996 | 1110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68345.65 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77602.0665 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84721 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92050.7331 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96735.9 | 762 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2574 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4383.1666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5125.5 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5736.0332 | 182 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7996.9999 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31893.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32288.6664 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34562.4998 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53588.3328 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70413.4 | 82 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 80323.485 | 598.61 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 54146.2496 | 675 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 13788 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3058.8499 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 16732.9999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 58181.375 | 788.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 63125.9333 | 96.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 21292.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 4753.1999 | 153 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 24401.6665 | 605 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1303.5 | 47.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23503.7999 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26193.4499 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32342.7282 | 354.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36753.3998 | 453 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40000.3332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61591.6665 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4681 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15729.6 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16749.6666 | 218 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32134.6665 | 440 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49299.25 | 385 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63301.333 | 440 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6695.1666 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7599.2498 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 40353.7498 | 675 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 33562.0697 | 517.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 20140.2 | 335.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 761.8986 | 51.02 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14193.6831 | 607 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35775.7999 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3762 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4024.5332 | 176 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29098.6665 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72784.3331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18795 | 420 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36090.9164 | 815 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.75 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.4166 | 55 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 825 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1300.6499 | 117 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 652.6665 | 178 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 807.3 | 351 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6747.3333 | 145 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.2667 | 19 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1000 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 854.4732 | 191.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 225 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 2155.5 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 724.5833 | 23.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 806.2167 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 4709.6 | 23.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 180.95 | 10.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 320 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 370.3333 | 11 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 206.1 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 78703 | 211 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 221.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 323.9333 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 416 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 14039.6882 | 241.37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15173.3999 | 99 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 16879.2568 | 242.46 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17201 | 412 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20190.1665 | 229 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22185.9 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25369.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25713.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27092.4331 | 607 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27353.75 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33177.2332 | 331 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35065.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42297 | 613 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51656.7329 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95413.9664 | 773 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348.3 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4480 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4546.3329 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5641.9 | 223 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7164.72 | 64.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11270.6 | 218 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12183.3332 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13341.5498 | 489 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24094.2662 | 628 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41512.5329 | 671 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64241.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70844.6697 | 815.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95504.7328 | 812 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96076.9997 | 870 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127781.5 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1008.6666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4415.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5005.4666 | 173 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7477.1666 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17706.6666 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19052.8 | 229 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23803.9999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27668.3332 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39292.2 | 498 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41448.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 12151.9999 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 10371.6 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 44553.6665 | 220 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8413.5 | 142 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 10570.5 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11034.4997 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 20217.25 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 25931.3266 | 100.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 29213.7666 | 239 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 43371 | 732 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 29920.2 | 564 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 668.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2701.8666 | 68 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5990.5999 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9938.1999 | 222 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20097 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48866.4997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 57342.9079 | 641.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21553.3996 | 606 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 38451.35 | 427 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 86998.4499 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5253.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13468.4663 | 532 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20863.5666 | 191 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13714.4333 | 226 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 19690.9999 | 420 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11 | 2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1323 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1749 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1961.2666 | 52 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 84.475 | 54.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 124.35 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2242.5333 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 243 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 362 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 718.4167 | 23.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 484.8 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 184 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6435 | 858 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3393 | 135 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3838.3332 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10536.6666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18719.0997 | 486 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25092 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27391.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30480 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38276.4996 | 1110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40549.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49567.6664 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51442 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55748.3329 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66330 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80894.6662 | 718 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175303.9997 | 816 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 798.1831 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3034.4999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3508.8 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5112.8 | 176 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5270.6666 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9403.3333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9599.3332 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14995.7498 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20342.2 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27107.5 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28824.3665 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43386.1832 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52996.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56619.8328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13116.0666 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15093.6706 | 241.37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16064.4 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18109.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19904.5831 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22445.4163 | 523 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24723 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25554.9333 | 244 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28792.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35194.25 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86541.6662 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130706.6664 | 800 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38136 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 10892.7 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 17231.6665 | 422 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10802.0832 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 30012 | 732 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 67833.15 | 539 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 14476.8 | 62.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 87322.95 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14976.4332 | 442 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17894.9999 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20381.7998 | 606 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60184.8331 | 790 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11733.3999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18532.8 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4110.3333 | 95 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12372.8 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16574.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37108.5 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52605.933 | 476 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14791.4166 | 197 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62496 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14461.8832 | 191 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48700.575 | 655.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2020.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18943 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1931.25 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2733.25 | 65 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3131.8333 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 603.1666 | 70 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2354 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 182 | 4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 338 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 420 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3639.5333 | 154 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 312.75 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 290.6667 | 16 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 516 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 616.1 | 18.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 421.6667 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6768.6998 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124669.133 | 871 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2588 | 48 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6412.1661 | 790 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7188.3 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9388.95 | 159 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10006.3833 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10051.25 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13844.3331 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16653.1666 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24203.9 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32777.3332 | 496 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51605.8997 | 471 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73052.4999 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76387.9997 | 780 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95508 | 758 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165273.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2053.3332 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2548 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3467.9999 | 306 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6314 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7991 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8570.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11604.6664 | 412 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13976.6333 | 229 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21742.9333 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24427.4999 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31506.5 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34249.9665 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38968.3498 | 639 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90857.3328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 936 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2922.8333 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3284.4 | 184 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5480.3331 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9017.0666 | 176 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13454.9999 | 135 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20183.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75250.4163 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161391.9991 | 1320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1833.9997 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1633.308 | 31.44 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 7320.61 | 134.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7921.8333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 9787.5 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 20884.6999 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 20968.9616 | 338.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 91204.2 | 414 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 12593.3332 | 400 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 17204.497 | 445.52 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 10865.2175 | 434.03 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 42209.4175 | 434.03 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 4722.8333 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3067.0833 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11347.8999 | 222 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30022.2497 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46137 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141353.3331 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19708.3999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32295.15 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64281.2499 | 255 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72599.9998 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86184 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68384.7996 | 528 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87690.8631 | 652.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11904.75 | 195 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20877.1164 | 839 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12824.7996 | 565.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16483.5 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10435.1666 | 127 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.72 | 84.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 572.7333 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 702 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 908.9998 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3082 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 342 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1070 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 524.1 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 309.4 | 364 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 1378.6667 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1909.5 | 19 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2102.9999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8584.6665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9237.0833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10131 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15580 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18008.6664 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21142.6 | 244 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21507 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29705.4999 | 363 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31917.6 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38123.7332 | 412 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70362.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86327.9998 | 594 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117702.99 | 815.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2495.4333 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2618.6666 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4501.3333 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5004.45 | 99 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5226.6 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6059.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7077.6666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8166.6665 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9015.4165 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16162.4999 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19877.0665 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30006.6665 | 560 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44947.5 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70497.4329 | 614 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88134.1996 | 1239 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115862.5 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116954.9 | 773 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 681.1666 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3683.3333 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3892.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6327.7663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6770.1331 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8897.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9165 | 780 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12831.4999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15901.3349 | 242.46 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16508.2497 | 783 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19028.3332 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25671.9 | 498 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 27709.1369 | 242.46 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31068.6663 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34594.3331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48778.6666 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52873 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72929.9997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99900.5 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74326.9329 | 602 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41969.6331 | 598 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 43533.3062 | 642.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14598.5 | 602 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 5727.4999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 11074.3466 | 340.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 32849.8332 | 259 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 63666.85 | 533 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 78672.2497 | 411 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4646.4 | 528 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4836.3 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 69725 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 29704.2 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 1511.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 34375.176 | 434.03 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 2270.46 | 47.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 5746.46 | 47.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10852.25 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22222.8999 | 318 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30536.9164 | 385 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48217.3331 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94726.6665 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17716.8332 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5542.9333 | 76 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8475 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69789.3333 | 160 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5480.4998 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72404.9995 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.3165 | 587 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 442.1666 | 70 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 599.25 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1038.6667 | 41 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1395.1 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2125.9 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4498.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 748.77 | 22.69 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1448.85 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20840.6664 | 430 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 658.95 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 679.2667 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 312.9167 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 818.75 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2022.5 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3874.1 | 57 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5721.3 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6052.0833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6097 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6176.6666 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7041.8333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10030 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10164.2999 | 153 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12067.4333 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15843.3332 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16030.4165 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19421.2499 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22464 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27550 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27842.4999 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36001.3331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36100 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36119.4998 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43537.5 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54863.1 | 846 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89261.9 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89608.1 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94733.7831 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1267.2 | 48 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2313.15 | 63 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3266.6665 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8658 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12542.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13749.9665 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13840.5832 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14308 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 14990.7766 | 238.58 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15572 | 229 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20776 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38109.8664 | 448 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 73873.9 | 659 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75808.9998 | 492 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120069.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 638 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3839.5665 | 503 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4171.4998 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4649.5 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8032 | 251 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11604.1249 | 97.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11641.9332 | 266 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18106.8 | 316 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25094.6665 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31689.75 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52835.0831 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55084.1665 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55627.9999 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65085.8328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69722.7665 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2842.6999 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2924 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6747.9997 | 420 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7464.9166 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 56552.4831 | 338.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57680 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 3552.0833 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 17660.4166 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 62888.4778 | 788.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 22893.9 | 402 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 23597.709 | 445.52 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 5332.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30624 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11871.7498 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13395 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19439.1497 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50920 | 800 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9242.6666 | 160 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11712.635 | 216.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12017.55 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21069.9998 | 588 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36538.6665 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8591.3332 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 95881.5 | 858 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152819.3332 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8283.3332 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40234.6661 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1300 | 325 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2921.7283 | 65.78 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 34790.02 | 358.66 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 41689.2 | 347.41 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 96.6667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 7012 | 350.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 8850.4166 | 275 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 2197.0333 | 38 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 4003.9999 | 429 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2221.02 | 370.17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 19867.92 | 348.56 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 1467.5185 | 446.96 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 43174.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 22.3331 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2218.02 | 369.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 13783.92 | 174.48 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 40674.0332 | 233 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 8360.88 | 348.37 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 27511.5331 | 330.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 6160 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 9568.8 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2143.02 | 357.17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 81262.94 | 354.86 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3783.7333 | 112 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 5600 | 112 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4720 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 45282.5 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1404 | 351 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 2055 | 342.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 767.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1551.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 430 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 609.4843 | 24.86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 603.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 648.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1939.3333 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 380 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1174.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 24.5833 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 67.2 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 432.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 565.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 578.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 761.3 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 885 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 477.75 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 499.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 555 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 43.9833 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 468 | 39 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 830.3 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 774 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 15.95 | 11 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 845.25 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1188.7333 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1568.6666 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 854.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 964.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1080 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 6.3 | 7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 123.05 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 364 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 424.6667 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 431.55 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 672.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1052 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 500 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1172 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 424.8 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 8098.0665 | 268 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 11082.9331 | 278 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 652.668 | 11.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 56.2683 | 0.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 368.8333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2651.9166 | 55 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1290 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2728 | 55 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 8921.85 | 293 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2098.3999 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 34079.9999 | 288 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 36547.2 | 288 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 826.4325 | 10.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 59.461 | 2.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 137.352 | 2.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1497.4167 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1515 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 139.68 | 2.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 680.1667 | 11 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 769.9815 | 11.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 13862.4999 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 458.7353 | 12.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 737.5167 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 107.3305 | 2.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 183.9 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 432 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1034.4 | 16 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2194.1558 | 24.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 12544 | 224 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 850-Combined Cycle Block
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 332.5 | 38 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40987.9165 | 611 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20867.9998 | 720 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2204.1333 | 61 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15382.1583 | 65.9 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30315.7829 | 611 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1765.4166 | 95 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 14937.315 | 335.67 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 10671.1333 | 118 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35378.7499 | 165 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16766.6166 | 191 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 780 | 390 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 23500.5731 | 338.3 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97425.2 | 604 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4510.5 | 62 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 392.7 | 51 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24752 | 85 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 48093.75 | 81 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7429.5 | 390 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9967.9999 | 210 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7079.3332 | 370 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45875.9165 | 611 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2493.9998 | 258 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 18576 | 258 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 552.1533 | 59.8 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 850-Combined Cycle Block
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11834.25 | 155 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 37633.0253 | 45.59 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 622 | 30 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 16388.32 | 62.4 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 3556.475 | 46.5 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8538.25 | 85 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9421.5 | 330 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1974.32 | 29.6 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 1395.5166 | 31 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30214.6664 | 340 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18196.8 | 446 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3056.9 | 21 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13770.7996 | 597 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15157.9666 | 62 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17078.9333 | 62 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 578.45 | 23 | 1 | 1 | 1005-Generating tubes | D2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9043.9999 | 168 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1645 | 84 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1650.75 | 46.5 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47164.6998 | 318 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1159.1 | 67 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 650-Fluidized Bed
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 10645.1833 | 67 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 650-Fluidized Bed
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 19547.25 | 67 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 650-Fluidized Bed
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1398 | 20 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 285.5667 | 26 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 636 | 12 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 240.8 | 30.1 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 548.6667 | 20 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1386 | 28 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1059.5 | 26 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 67.0833 | 35 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 851-CC GT units
1005 | Generating tubes | HRSG Boiler | HRSG Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | NPCC | Summer | 7453.8 | 41.41 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 851-CC GT units
1006 | In-bed reheat tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 21888.5832 | 155 | 1 | 1 | 1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5383.5 | 30 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 444.1666 | 65 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3361.5 | 45 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16189.5 | 45 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30744.9998 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 516 | 45 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5602.5 | 45 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32378.9999 | 90 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D3-Forced - Postponed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 256.98 | 42.83 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24797.25 | 45 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2443.5 | 45 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5893.1245 | 175.13 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15417.3332 | 248 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21361.9999 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41866.9999 | 210 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 419.3333 | 40 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 612 | 80 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 568 | 17.75 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 2466 | 308.25 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 4036.08 | 168.17 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6959.97 | 409.41 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 12609 | 350.25 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 23437.94 | 349.82 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 19130.16 | 341.61 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 51717.58 | 354.23 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 430 | 86 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2707.1664 | 439 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 8501.9664 | 439 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 73811.8 | 181 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 213.3 | 79 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82845 | 263 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45185 | 700 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39822.3 | 602 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5110.7 | 68.6 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17594.7 | 446 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8552.1 | 174 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25368.75 | 825 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18108.1831 | 577 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12609.9665 | 199 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42037.5995 | 816 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79916.6662 | 700 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18958.1999 | 342 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 34729.5 | 411 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14460.8999 | 342 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22207.1999 | 342 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24185.0998 | 342 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 169.8666 | 91 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11437.5 | 150 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6882.8665 | 602 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 582.9999 | 318 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2033.3332 | 200 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38811.2999 | 342 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106639.5 | 1265 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1330 | 350 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112.5333 | 21.1 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25146.9665 | 446 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7418.6 | 196 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3100.0665 | 196 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34524.5331 | 598 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61687.9996 | 1320 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8269.8331 | 290 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 523.25 | 13 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 800-Miscellaneous
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 243.75 | 13 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 800-Miscellaneous
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2477.9333 | 62 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 800-Miscellaneous
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1296 | 45 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1441.5 | 30 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1125 | 20 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27289.5 | 210 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52968.7497 | 1017 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 785.52 | 10.91 | 2 | 2 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67593.3332 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11994.9999 | 300 | 2 | 2 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70 | 20 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 828 | 34.5 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65166.6661 | 850 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 404.88 | 19.28 | 2 | 2 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47905.9998 | 510 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7003.3333 | 220 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59795.8329 | 635 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80736.6666 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.92 | 6.64 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 708 | 29.5 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 37057.7333 | 136 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 650-Fluidized Bed
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1204 | 28 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 800-Miscellaneous
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 460.7 | 27.1 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 800-Miscellaneous
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8187.1997 | 816 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18925.5 | 555 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86337.4995 | 750 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106837.2 | 531 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 977.5 | 230 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54952.5 | 510 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206271.4664 | 881 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59469.9996 | 600 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 369.1665 | 443 | 1 | 1 | 1035-Platen superheater | D2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57044.833 | 515 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5010.8333 | 175 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28285.1662 | 745 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 446.9999 | 180 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45610.9998 | 510 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2884.9666 | 106 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52717.8331 | 670 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68562.6665 | 280 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 69114.4997 | 390 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10003.5 | 171 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52223.85 | 531 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39337.8499 | 249 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28989.9999 | 390 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41310 | 405 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8636 | 635 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 4009.9999 | 120 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25444.8 | 342 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73205.9999 | 270 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 249528.5664 | 881 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 670542 | 552 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67107.42 | 815.4 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35959.9998 | 600 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 109170.5827 | 881 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84507.8328 | 830 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44080.9998 | 510 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24506.04 | 358.8 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 33184.6665 | 280 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 40646.6665 | 280 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 69374.6665 | 280 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2163.95 | 191.5 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 280 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10588.8 | 72 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3382.5 | 55 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12730.3333 | 181 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26321.3333 | 190 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2931.35 | 69 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10143.0333 | 178 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18291 | 156 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47531 | 580 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 58365.9997 | 420 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 90906 | 436 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15767.2165 | 187 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18512.3331 | 380 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 32363.8999 | 222 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5258.6666 | 290 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8651.4999 | 78 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17231.7999 | 174 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20774.1665 | 485 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35031.3332 | 340 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5679.1666 | 290 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37358.0831 | 335 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 382.21 | 10.33 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 9.3333 | 70 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 39.9999 | 150 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31761.6661 | 850 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3301.6667 | 50 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10193.5999 | 276 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26894 | 340 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12027.1666 | 182 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18649.7 | 65.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52071 | 510 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 16676.7066 | 137.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 38909 | 533 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 33858.333 | 500 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38235.6 | 152 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 43217.3 | 577 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2453.6666 | 85 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14521.1666 | 151 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24728.5831 | 335 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26535 | 580 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93000.5329 | 614 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23404.5 | 630 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 309.8332 | 286 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2563.45 | 167 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9756.5 | 190 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18803.65 | 197 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24833.6666 | 290 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25214.9999 | 225 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31930 | 412 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11856.65 | 481 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13307 | 140 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15633.445 | 466.67 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 8834.3332 | 170 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 5150.4693 | 59.36 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6996.9166 | 85 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23744.2 | 523 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25515.8331 | 335 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115385.8329 | 650 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 10260 | 75 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7800.5332 | 412 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8098.2497 | 435 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4102.6666 | 85 | 1 | 1 | 1040-First superheater | SF-Startup Failure | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4358.7 | 167 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6848.8331 | 290 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30300 | 505 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53389.9996 | 570 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 56933.74 | 466.67 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10116.6 | 156 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18714.5 | 105 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27708.3329 | 665 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8974.5833 | 175 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98509.6665 | 635 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10807.2 | 474 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21451.9665 | 178 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8058.6499 | 159 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9479.0499 | 159 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5415 | 285 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9850.2333 | 151 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 54946.6663 | 520 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 346.6666 | 200 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 565.4167 | 23 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29050.6663 | 520 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37469.9997 | 450 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43524 | 124 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19856.9 | 266 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38028.9997 | 510 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38389.6333 | 154 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7559.3331 | 290 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9250.1833 | 199 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11000 | 200 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22983.6665 | 380 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71372 | 560 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3775 | 151 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6840.5333 | 121 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68026.8997 | 474 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1976.6666 | 50 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3896.2166 | 157 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2.5 | 30 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 127 | 127 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 383.3332 | 230 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.4166 | 31 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8160 | 85 | 1 | 1 | 1040-First superheater | SF-Startup Failure | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6060.4833 | 181 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10374 | 190 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18908.25 | 255 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14539.3833 | 127 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43689.9997 | 510 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71554.1665 | 650 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5959.6665 | 190 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10872 | 151 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42271.9166 | 85 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4077 | 151 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4400.19 | 77.4 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7305.45 | 129.3 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35397.25 | 565 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36740 | 440 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2571.3331 | 290 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2767.2633 | 101.8 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 750 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 640.1833 | 71 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.96 | 16.6 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1484.4 | 72 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1821.2 | 58 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3189.9998 | 330 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5643 | 285 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14219.7666 | 254 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17274.8331 | 670 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44199.9997 | 510 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154857.0831 | 565 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6437.1533 | 101.8 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106219.5 | 570 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14539.8 | 132 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26563 | 505 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7391.6499 | 129.3 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61316.6664 | 650 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7852 | 151 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11148 | 120 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56089.8332 | 262 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5791.5 | 135 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36843.1 | 721 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1161.27 | 16.83 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 3.3333 | 40 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 35 | 175 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3585.9998 | 330 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7187.9999 | 180 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7689.0399 | 129.3 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27687.3331 | 595 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45866.25 | 405 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189690 | 600 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3399.5 | 523 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17534.3663 | 493 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2519.52 | 104.4 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5387.45 | 57 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6795.75 | 117 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9205.9666 | 151 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25977.6 | 264 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 57081.9832 | 397 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 64254.6662 | 715 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5217.6666 | 55 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49213.6665 | 554 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25845.0666 | 152 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29585.6664 | 340 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42021 | 580 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27156.1215 | 216.7 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6393.4999 | 285 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10810.4499 | 201 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2134.4 | 69 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1432.1666 | 32.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 39904.1663 | 610 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 29145 | 335 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4966.1333 | 35.2 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 22.75 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 132.215 | 9.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 135.6 | 11.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 404.0667 | 44 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 56.8333 | 11 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 113.3 | 10.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1472 | 23 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 323.125 | 14.1 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1181.2 | 24 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 321.2 | 7.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 398.4 | 8.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 440.425 | 22.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1201.6667 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 74.5833 | 25 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 247.9167 | 25 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 289.325 | 16.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 401.7 | 26 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 26.45 | 23 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 190.495 | 9.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 525 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 32 | 16 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 278.6833 | 23 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 14.4666 | 31 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 181.355 | 8.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1375.7833 | 23 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 158.1 | 9.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 326.4667 | 8.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 114 | 24 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2620.0833 | 23 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 55296.5 | 518 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1071.5 | 30 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 57384 | 288 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 221.25 | 9 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 33792.35 | 419 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 3059.2833 | 37 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 13093.75 | 419 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 25615.1 | 518 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 639.1667 | 26 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 962.6667 | 10 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2984.2666 | 31 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2480.5 | 30 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 15052.1332 | 158 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 851-CC GT units
1040 | First superheater | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 9336.1333 | 98 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 852-CC steam units
1040 | First superheater | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1130.8333 | 46 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 852-CC steam units
1045 | In-bed superheater tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 27001 | 268 | 1 | 1 | 1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1675.5999 | 177 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10027.6 | 473 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 763.4 | 44 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1495.89 | 302.2 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1058.7667 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 811.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11986.6666 | 290 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33486.75 | 615 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36396.0829 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51530.25 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69348.0665 | 497 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6207.1333 | 32.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19637.8331 | 290 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20713.9333 | 196 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25432.2 | 639 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99106.7327 | 971 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2124.2 | 78 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14845.2999 | 159 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20176.6666 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3631.0666 | 113 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8085.5 | 157 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19460.9332 | 406 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 45689 | 749 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42707.3331 | 580 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8030 | 275 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31408.9996 | 588 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32182.4998 | 315 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31547.3331 | 395 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 14658.3332 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30150.7498 | 315 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.15 | 39.83 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 90.545 | 27.3 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 753.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 900.45 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9056.6666 | 275 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3354 | 156 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95571.8329 | 593 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4745.5832 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8003 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10672.6666 | 140 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18002.25 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55938.9998 | 507 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2960 | 74 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 47016.6665 | 500 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1752.6 | 46 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95609.8329 | 635 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11508.3 | 342 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33160.1542 | 662.32 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 29976.9165 | 455 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5738 | 151 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 81236.25 | 747 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 713 | 92 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 613 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9302.1 | 614 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17018 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 60557.4663 | 598 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92454.6331 | 577 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13288 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17214 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20938.0666 | 127 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53949.5825 | 1325 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69265.233 | 497 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13794.6 | 554 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20182.2496 | 615 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94449.1661 | 850 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1258 | 74 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 6480 | 135 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33745.25 | 385 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 58912.9331 | 658 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83160.6665 | 395 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 690.3833 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 117 | 260 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 148.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 538.3333 | 50 | 1 | 1 | 1050-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2986.5166 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22187.5662 | 661 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104681.5 | 770 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106596.25 | 1325 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9614 | 190 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 167962.4991 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 3108.481 | 28.97 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11680.3332 | 523 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18567.4664 | 412 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22791.7665 | 371 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34176.25 | 475 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14886.6666 | 200 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17011.9999 | 240 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31449.9999 | 255 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5840.9999 | 135 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52526.8332 | 385 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 972 | 24 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6123.9 | 137 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 164.64 | 3.43 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 588.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 735.2667 | 26.9 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 849 | 18 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1245.9 | 18 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10169.7499 | 285 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16076.6665 | 280 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3382.5999 | 156 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4127.65 | 93 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4429.3333 | 160 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6088.5 | 135 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10444 | 140 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38555.9881 | 655.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40399.9998 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47629.36 | 29.6 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3217.6666 | 98 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31330.1665 | 593 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36685 | 638 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29367 | 780 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 33695 | 575 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 4585.7413 | 28.64 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7643.2 | 108.8 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 29473.1663 | 610 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19240.4 | 412 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 52935.7499 | 135 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35177 | 580 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21220.7499 | 435 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 291.2 | 24 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 583.1 | 119 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 605 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4397.6666 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25039.7496 | 555 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2430.4 | 93 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5322.3 | 157 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44209.9998 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2067.8 | 98 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10635.1616 | 65.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11658.6 | 254 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15486.6666 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 33286.2 | 174 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4308.3332 | 275 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11139.195 | 129.3 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 78507 | 610 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11439.1332 | 197 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 312 | 26 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203.55 | 69 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 472.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 664.2 | 18 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2174.65 | 93 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25501.4665 | 614 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56092 | 740 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62469.8663 | 577 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1091.15 | 157 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3617.25 | 159 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10176.25 | 175 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27491.2499 | 225 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57084.5331 | 577 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6079.2666 | 98 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12382 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45048.61 | 65.4 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 50325 | 500 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20629.5832 | 385 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65527.1164 | 469 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 16082.6664 | 370 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 111.15 | 22.23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 205.52 | 29.36 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1308.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 83.9166 | 26.5 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 51030 | 405 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3560.35 | 93 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3879.75 | 63 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18733.9998 | 228 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49378.3329 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3192.3333 | 157 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3205.3999 | 93 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6221.7999 | 156 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14334.4166 | 185 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54705.3 | 507 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4309.5 | 510 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13253.3332 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21746.6666 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47569.1664 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 12400.6665 | 380 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5637.3333 | 151 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47732.5997 | 417 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 140322.4993 | 1110 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 11814.7499 | 135 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2532.6663 | 580 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 15302 | 280 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 22941.9166 | 335 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 4650 | 100 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 25719.0665 | 268 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 855.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 67.8 | 11.3 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 235.8 | 13.1 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 226.8 | 8.1 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1905.3333 | 40 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 806.4 | 42 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1233 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 100.8 | 32 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 265.6 | 8.3 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1582.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1343.5667 | 17 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1174.1333 | 14 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1403.1 | 27 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2057.0667 | 29 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2291.9667 | 29 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2934 | 30 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 6299.5 | 293 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 572.8 | 16 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1194.2667 | 13 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2204.8 | 24 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 71984 | 55 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2514.7666 | 37 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2039 | 30 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 906.3 | 318 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 15151 | 278 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 253.75 | 15 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 795.8833 | 17 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1544.95 | 33 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1991.25 | 81 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 851-CC GT units
1050 | Second superheater | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 3631.4999 | 162 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 852-CC steam units
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59317.9994 | 840 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 194.0833 | 17 | 1 | 1 | 1055-External superheater link tubing | SF-Startup Failure | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30439.05 | 307 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6523.9994 | 840 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49855.6329 | 602 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 1697.938 | 24.86 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 800-Miscellaneous
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21606.8 | 114 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 48283.4166 | 73 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3735 | 15 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2448 | 68 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4359.4 | 614 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33355.25 | 505 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65166.833 | 494 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432.9332 | 191 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37064.1665 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66086.1332 | 158 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 77597.1662 | 670 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54368.1663 | 598 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7266 | 840 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7693 | 157 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 56258.6666 | 170 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52652.0829 | 635 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63098.6093 | 736.13 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27084.8332 | 505 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41522.4997 | 510 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14885.1666 | 155 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32818.3331 | 580 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9642.3166 | 191 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82804.9 | 251 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22809.6665 | 205 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 85910.7165 | 533 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 49959.8665 | 533 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8907.5 | 15 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15659 | 70 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 37593.7833 | 73 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1169.8833 | 17 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 16606.7999 | 108 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 52601.25 | 83 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28802.4998 | 615 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42864.0831 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46596 | 440 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16107.465 | 261.91 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35544.6 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135834.5824 | 1325 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4975 | 199 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53969.3332 | 340 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 64969.1385 | 598.61 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8312.2 | 598 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 56423.5996 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9160 | 458 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29441.5 | 505 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8130.8332 | 275 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19228.559 | 261.91 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22342.3831 | 401 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 85583.3329 | 650 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32509 | 580 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6736.6666 | 200 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14250.6666 | 320 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24333.8 | 842 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23700 | 300 | 2 | 2 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28824.9999 | 300 | 2 | 2 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2594.4962 | 166.67 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3003.2166 | 167 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 32856.8832 | 233 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 6961.5 | 35 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.5467 | 17.6 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 471.21 | 33.9 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7440 | 10 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7763.5999 | 156 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65186.7998 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20824.9165 | 235 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28260.3164 | 839 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51084.3329 | 662 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 46282.5 | 450 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 45326.7996 | 564 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7961 | 95 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15015 | 260 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78930.9997 | 510 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104681.5 | 770 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3697.6333 | 91 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8795.5 | 245 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5289.75 | 15 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1525.6666 | 230 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3783.7499 | 225 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20505.3333 | 208 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 54836.7166 | 83 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7275.6667 | 10 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 23177.9499 | 213 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3621.3332 | 280 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26577.8329 | 665 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34912.5 | 465.5 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145454.6665 | 590 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26852.5099 | 437.1 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28467.1999 | 192 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113508.3325 | 1325 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116047.9162 | 1325 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7875.5 | 190 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82990.0664 | 659 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114803.3329 | 620 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47502 | 840 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2714.3333 | 85 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20565.9999 | 390 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29853.3747 | 261.91 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16696.7499 | 435 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16900 | 200 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27165.6666 | 260 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23100 | 840 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11154.75 | 417 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 48439.15 | 577 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36207.9166 | 335 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36370.1 | 554 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34199.8 | 614 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113750 | 520 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 13493.55 | 213 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11755.2 | 186 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 25002.3666 | 83 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 331.8669 | 211.83 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46920 | 85 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9118.0832 | 245 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13340 | 580 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39154.9999 | 150 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40413 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8534.1666 | 245 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28158 | 247 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12610.7169 | 598.61 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15855.3332 | 340 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56905.6665 | 620 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20151.6666 | 100 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39913.6663 | 580 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 156583.6663 | 505 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30085.9996 | 588 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30508 | 580 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 15386.583 | 455 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5894.7499 | 285 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59902.4998 | 630 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52449.2498 | 615 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 207.5 | 15 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 167.28 | 27.88 | 2 | 2 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 36128.9666 | 103 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14865.15 | 339 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27876 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42822.8467 | 390.66 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 60822.6565 | 466.67 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69826.6664 | 800 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76045.3333 | 160 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83656.9993 | 1110 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108280.5 | 1110 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52884.8328 | 830 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65758.7663 | 577 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121502.5 | 1325 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21354.9999 | 300 | 2 | 2 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19532.4999 | 390 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 202.4167 | 35 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 249.1666 | 130 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17493.5 | 295 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3511.2499 | 159 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2391.6665 | 350 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20472.1996 | 588 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12510.5 | 262 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17636.6665 | 220 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64300.7332 | 158 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8957.95 | 97 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25483.843 | 261.91 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28746.6833 | 247 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34630.6665 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59944.5 | 630 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62272.083 | 515 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79201.4996 | 630 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89496 | 1320 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8937.5 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 159143.6665 | 620 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | NPCC | Off-Peak | 6270.3958 | 147.25 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25116 | 598 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41277.4998 | 627 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19055.8999 | 174 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85624.1873 | 736.13 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114142.6 | 614 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 16366.9332 | 448 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6099.25 | 93 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 51780.8664 | 749 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 22819.3999 | 213 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6393.9166 | 97 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95338.7499 | 195 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 117.88 | 29.47 | 2 | 2 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 990 | 180 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1585.65 | 341 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 543.9333 | 82 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.3367 | 13.4 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5355 | 85 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60752.6999 | 162 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129210 | 590 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9501.9166 | 245 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18322.4998 | 315 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25415.7332 | 191 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71651.0832 | 505 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16268 | 245 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36430.5 | 815 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 50304.6663 | 610 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 650-Fluidized Bed
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1082.5 | 25 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 800-Miscellaneous
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 47895.8831 | 769 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1224 | 288 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1060 | First reheater | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 9432 | 144 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 851-CC GT units
1060 | First reheater | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 9392.5 | 102 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 852-CC steam units
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122.85 | 63 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1541 | 670 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.9666 | 122 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 76.8165 | 419 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 373.6999 | 303 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30039.8 | 602 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88510 | 1325 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43520.3331 | 685 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6943.8499 | 339 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3822 | 390 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4142 | 760 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19791.9998 | 240 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2791.6832 | 167 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3918.9332 | 167 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25548.55 | 523 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20528.6665 | 280 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27705.75 | 255 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6807.1999 | 201 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19884.3333 | 220 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11793.9165 | 307 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108249.1664 | 770 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38359.8 | 606 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35582.2996 | 606 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 8509.5 | 135 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27467.1833 | 187 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 193 | 38.6 | 2 | 2 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9492.2333 | 238 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30175.25 | 401 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 320.1666 | 170 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 493.35 | 299 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 124427.2328 | 773 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4774 | 770 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12727.19 | 158.2 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24053.45 | 307 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16705.3332 | 340 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4749.7666 | 113 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39400.9 | 602 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35433.1666 | 290 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9004.3333 | 238 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26350.85 | 493 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4619.55 | 103 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13959.2666 | 218 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57241.8 | 531 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 910790.8329 | 650 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35215.3332 | 523 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 522.6 | 268 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9230 | 130 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11947.6 | 238 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18709.35 | 493 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7433.5996 | 606 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16800 | 300 | 2 | 2 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2875.9749 | 203.01 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122971.4164 | 773 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14337.2 | 491 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119309.2 | 758 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139241.6665 | 620 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24694.2 | 459 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 944.5332 | 161 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 852-CC steam units
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5585.9999 | 180 | 1 | 1 | 1075-External reheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11616 | 176 | 1 | 1 | 1075-External reheater link tubing | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 230 | 230 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5286.75 | 265 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8566.25 | 175 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13437.1999 | 168 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17504.6999 | 342 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74587.5 | 1350 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5984.55 | 99 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19666.2666 | 266 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24632.7498 | 555 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21151.5 | 590 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2384.88 | 52.3 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37795.3333 | 178 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 28538.6033 | 333.33 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3891.6666 | 100 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61893.8665 | 416 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75825.3331 | 580 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115518 | 520 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3733.9499 | 99 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 43180.0831 | 655.9 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1615.0999 | 93 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140 | 140 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 358.6333 | 7 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 856.8 | 476 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13678.3331 | 580 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41370 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51238.6664 | 830 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55689 | 570 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6489.1332 | 218 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1296.75 | 63 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5489.4 | 63 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6505.54 | 49.8 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80879.1995 | 816 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2021.25 | 825 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 8490.0999 | 354 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 20336.25 | 435 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 27056 | 178 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9280 | 100 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33677.4998 | 570 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 3631.65 | 46.5 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.4 | 117 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 484.5 | 190 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2601 | 340 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3716.6666 | 125 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 614.4 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 2336.25 | 31.15 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4930 | 100 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16811.6666 | 100 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 21657.9997 | 420 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5816 | 48 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9301.05 | 99 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12219.9998 | 240 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1956.875 | 46.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 39121.3331 | 610 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8951.3333 | 145 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38730.6666 | 160 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8823.9998 | 240 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 8 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 258.6666 | 80 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1035.9166 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4116 | 168 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4479.75 | 99 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9227.3999 | 117 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14433.3333 | 100 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16453.7333 | 244 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41569.9998 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50370 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108867.9995 | 816 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4577.1 | 99 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36560.9165 | 485 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3461.6 | 48 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43435 | 425 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4303.7495 | 825 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6945.9999 | 345 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 6522.1568 | 333.33 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1052.8 | 47 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19776.3998 | 588 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2430.8959 | 180.96 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2435.4 | 99 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16022.8997 | 489 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45761.6 | 773 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 532.95 | 104.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2537.3832 | 239 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14674 | 667 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 3582.9 | 81 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 9368.0833 | 79 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66 | 110 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 230.4 | 96 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.8333 | 70 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1125 | 375 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1750.3 | 69 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7926.45 | 63 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11925 | 265 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24079.9664 | 394 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39687.3329 | 590 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2839 | 167 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12422.3 | 491 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17008.7494 | 825 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1979.325 | 51.3 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 49771.2665 | 524 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 11852.58 | 337.2 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10284.45 | 253 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4263.6 | 88 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5605.0166 | 107 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2776.2533 | 82.3 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170 | 170 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 280.3331 | 290 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2456 | 48 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43266.6664 | 800 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49560 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10091.3665 | 262 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19899.7998 | 564 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35850.033 | 467 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46540.5 | 690 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57680.0998 | 486 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79764 | 276 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1429.6 | 48 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44419.9998 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1236 | 103 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 16519.1666 | 215 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 157464 | 81 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2621.5 | 107 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 487.3333 | 20 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 6718.0333 | 43 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25382.7 | 474 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41924.4 | 552 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10599.5 | 290 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21663.3331 | 335 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11852.9999 | 162 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4.7 | 6 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340 | 170 | 1 | 1 | 1080-Economizer | D3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17838.3328 | 770 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54609.0996 | 546 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72618 | 570 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77513.7996 | 546 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38947.9997 | 780 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 39694 | 178 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11278.4 | 76 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 85854.0162 | 667 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 9749.9025 | 333.33 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1954.1666 | 67 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6988.3333 | 100 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10081.6666 | 100 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 357733.3328 | 800 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55640 | 800 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12305.6665 | 190 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3954 | 120 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1056 | 22 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 21641 | 67 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1820 | 32.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 2793.9 | 67 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 16023.0666 | 136 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 1541 | 67 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1140.2083 | 32.5 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 19919.79 | 349.47 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 9928.2833 | 67 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1056.7916 | 32.5 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4607.8 | 12 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 5033.9333 | 67 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1340.625 | 32.5 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 16.25 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 55.25 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 11 | 11 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 38.5667 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 56 | 16 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 91 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 208 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 228 | 24 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 961.3333 | 28 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 74.75 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 334.75 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 412.75 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 175.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1821.6 | 24 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 26 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 63.9167 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 84.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 474 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 11.4167 | 5 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 39 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 106.6667 | 32 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 369.9167 | 23 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 138.6667 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 483.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 562.3333 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2040.5 | 22 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 45.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 800 | Miscellaneous | NPCC | Winter | 820 | 20.5 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 463.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1001 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 230.75 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 286 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 533 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 286 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 383.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 389 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 472.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 628.3333 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 680 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 16.4 | 41 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 87.5 | 21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 178.75 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 793.3333 | 25 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 136.5 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 945.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 69.3333 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 112.6667 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 143 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 199.3333 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 837.0833 | 25 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 997.9167 | 25 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 432.25 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 95.3333 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 218.8333 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 260 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 397.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 13782.3332 | 346 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 45128.4166 | 55 | 1 | 1 | 1080-Economizer | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1447.4166 | 55 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1760 | 55 | 1 | 1 | 1080-Economizer | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 15505.4166 | 55 | 1 | 1 | 1080-Economizer | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 896.5 | 55 | 1 | 1 | 1080-Economizer | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 12415.5 | 155 | 1 | 1 | 1080-Economizer | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 718.2 | 76 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 850-Combined Cycle Block
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1844.2666 | 104 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 850-Combined Cycle Block
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 6188 | 104 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 850-Combined Cycle Block
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | OG | 850 | Combined Cycle Block | MRO | Winter | 8394.9999 | 300 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 850-Combined Cycle Block
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 14916.8999 | 171 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 851-CC GT units
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 19455.9998 | 240 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 851-CC GT units
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | TRE | Summer | 25052.3332 | 170 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 851-CC GT units
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 730 | 73 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 851-CC GT units
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 1105.1665 | 190 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 851-CC GT units
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Summer | 778.6666 | 73 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 851-CC GT units
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 2199.45 | 133.3 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 852-CC steam units
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 458.6666 | 43 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 852-CC steam units
1080 | Economizer | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 430 | 43 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 852-CC steam units
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3613.7498 | 525 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 24583 | 155 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 22488.3999 | 228 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6903.46 | 70.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 11484.48 | 17.09 | 1 | 1 | 1090-Other boiler tube leaks | SF-Startup Failure | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34956.8329 | 665 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37054.9 | 307 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12699 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 104706.85 | 881 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6063.3332 | 200 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46662 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50100 | 600 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 10802 | 110 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 154560 | 483 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 3888.1095 | 115.89 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1080 | 45 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37555.8331 | 374 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8.6666 | 40 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.6666 | 70 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26.6666 | 100 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 252.1333 | 124 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1183.6666 | 335 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1672 | 190 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 85.5 | 114 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7850.7 | 143 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14742.65 | 613 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65352 | 336 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 851 | 37 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33800.7 | 307 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 621.25 | 35 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 18768.75 | 385 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26877.6667 | 35 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66191.6665 | 500 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 4110.0833 | 43 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16231.0832 | 155 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92004 | 615 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 7802.6665 | 380 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211.1666 | 70 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 196 | 60 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1122.4566 | 70.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 106.2 | 27 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 12714.96 | 17.09 | 1 | 1 | 1090-Other boiler tube leaks | SF-Startup Failure | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13790.4 | 156 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66997 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9773.75 | 175 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97328 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 793.0832 | 307 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2816.127 | 115.89 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43333.7333 | 232 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1147.3 | 21 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20634.5999 | 153 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1529.55 | 309 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.8333 | 50 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2418 | 120 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 357 | 12 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1435.8933 | 98.8 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 4212.6 | 126 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17896.6665 | 650 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19163.0999 | 198 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64698.6665 | 280 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23914 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203613.6664 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4597.4666 | 164 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12070.5665 | 238 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20198.2665 | 238 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27423.3665 | 638 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31770 | 600 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74270 | 700 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1321.4466 | 52.3 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 248.325 | 64.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 4262.048 | 59.36 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1061.55 | 21 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17613.7 | 442 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37335.4 | 278 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 126720 | 528 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2133.3332 | 400 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1637.6666 | 85 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1930.5 | 135 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 860 | 12 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 761.5667 | 22 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 469.4282 | 396.7 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16080.35 | 143 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14797.2666 | 173 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1184 | 37 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8580 | 330 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17061.333 | 560 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25001.3332 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30620.7328 | 842 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36699.8328 | 830 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153384 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61280.4 | 510.67 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 60950.8665 | 422 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 12296 | 424 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 27126.5 | 239 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 55211.733 | 542 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6221.4995 | 690 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5925.333 | 440 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 659 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3414.5832 | 149 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 680 | 340 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 9160.24 | 17.09 | 1 | 1 | 1090-Other boiler tube leaks | SF-Startup Failure | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3942 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24365.5665 | 307 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25721 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39028 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68387.3331 | 760 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9192.6833 | 101 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25613.3332 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38535.5 | 370 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2949.3333 | 35 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11431.1666 | 107 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39183.333 | 500 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66919.9998 | 600 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96750.5 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 101695.7499 | 435 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 74082.3665 | 542 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 227287.7 | 542 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1527.75 | 21 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23849.7999 | 156 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18101.0166 | 197 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33975.4 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.5333 | 43 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.5 | 90 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 408.75 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 553.3333 | 40 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2464.9166 | 55 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13338 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2146.8333 | 110 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 8732 | 74 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2576.224 | 59.36 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51097.2 | 264 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5702.9331 | 592 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28 | 80 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 427.25 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1360.3333 | 110 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1746.8166 | 163 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2551.3333 | 43 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 39918.9998 | 330 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41710.5 | 713 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6072 | 66 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6774.8833 | 107 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68350.5329 | 611 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 105148.3331 | 422 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 15482.6666 | 320 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 11082.2513 | 576.7 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 17005.4024 | 406.18 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27220.05 | 611 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21965.3333 | 160 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 577.5 | 21 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 716.45 | 21 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 14200.2664 | 376 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 11485 | 100 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Coal | OS | 650 | Fluidized Bed | WECC | Winter | 671.64 | 11.58 | 1 | 1 | 1090-Other boiler tube leaks | D3-Forced - Postponed | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 12406.1599 | 362.4 | 1 | 1 | 1090-Other boiler tube leaks | D3-Forced - Postponed | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 143.56 | 11.1 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 903.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 958.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 2359.6283 | 24.86 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1384.5333 | 22 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 616 | 22 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 702 | 26 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 969.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 756.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1434.8 | 24 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 433.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 815.8333 | 22 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 4271.3332 | 298 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 32850.3331 | 278 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1406.8333 | 23 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 850-Combined Cycle Block
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9282.2666 | 344 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 850-Combined Cycle Block
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Summer | 7487.7516 | 196.1 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 851-CC GT units
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 49.45 | 129 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 851-CC GT units
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 9660.8499 | 141 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 851-CC GT units
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | WECC | Winter | 5872.5 | 145 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 851-CC GT units
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2015 | Gas | GG | 851 | CC GT units | TRE | Winter | 2727.9333 | 83 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 851-CC GT units
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | U2 | Forced - Delayed | 2015 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 7079.3333 | 82 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 851-CC GT units
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 3847.5 | 95 | 1 | 2 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 852-CC steam units
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | D1 | Forced - Immediate | 2015 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 6259.0666 | 92 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 852-CC steam units
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.7666 | 158 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 412.3665 | 178 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 841.5 | 18 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2165.7333 | 148 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 823.75 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1114.75 | 49 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 22218.2333 | 61 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 3294.9999 | 300 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 436.1 | 178 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1396.05 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23.85 | 53 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2560.7833 | 13 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.8333 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177.9167 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255 | 90 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 220.8333 | 50 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 224.3333 | 10 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 333.3333 | 250 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 410 | 40 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2754.4 | 11 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 478.8 | 76 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6055.8333 | 26 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 81677.5 | 111 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 15097.3333 | 26 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 255.2 | 48 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468.7333 | 178 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 518.9999 | 90 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1115.1 | 118 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1729.5665 | 178 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.6667 | 20 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 20 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1659.7666 | 34 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 9682.35 | 51 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.0866 | 85.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 107 | 107 | 1 | 2 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53286 | 830 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5497.3333 | 76 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 11206.4 | 51 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 310.2332 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.20833 | 0.25 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276 | 138 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.3333 | 40 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 40 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2165.3667 | 38 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.3333 | 25 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.3333 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8056 | 38 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 745.3166 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 698.6999 | 153 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8183 | 28 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 397 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3097.5 | 25 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.5 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 992.25 | 49 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 45013.9333 | 61 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 181.9999 | 168 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 20 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 774.1998 | 237 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 56.75 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32855.9 | 374 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 298.9999 | 138 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.9333 | 49 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1320 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 453.08 | 48.2 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 65130.75 | 81 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 560.7 | 178 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 450.85 | 127 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 503.0666 | 28 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 761.6667 | 50 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3157.3333 | 148 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6754.5 | 18 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1620 | 120 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.2 | 19 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.5 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5916.6665 | 250 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 916 | 120 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 2307.9466 | 35.2 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32712.75 | 603 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40297 | 590 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 768 | 4.8 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175 | 10 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.5 | 21 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1932.32 | 10.4 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 991.015 | 5.1 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2646.5 | 79 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20 | 20 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 62.7 | 3.3 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 87.4 | 4.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 100.7 | 5.3 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 483 | 7 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.25 | 37 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 480 | 20 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6846 | 8.4 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 823.9333 | 4 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1005 | 6.7 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1092 | 5.2 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2015 | Coal | LI | 650 | Fluidized Bed | MRO | Summer | 9328.73 | 74.6 | 1 | 1 | 1105-Generating tubes | U2-Forced - Delayed | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | MRO | Summer | 1835.8667 | 5.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 2082.89 | 18.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 3313.8 | 12.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 4070.4 | 10.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 2980.3666 | 337.4 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 29410.0331 | 337.4 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16563.4333 | 199 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22294.0666 | 77 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.7466 | 53.6 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 278.3667 | 14 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1068.7717 | 16.1 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 109782.4 | 364 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.524 | 19.72 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D3-Forced - Postponed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37037.2165 | 199 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3237.29 | 30.9 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1842.3233 | 16.6 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 218.5 | 28.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 892.5 | 42 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.25 | 35 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 687.5 | 110 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2947.5 | 30 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3537.5 | 25 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12847.5 | 50 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 445 | 20 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 527.0833 | 5 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31157.4665 | 465.5 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | NPCC | Summer | 5554.5075 | 173.85 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 14 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119 | 7 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 724.5 | 69 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 972.9166 | 125 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2494.7 | 57 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4675 | 85 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3556.8 | 494 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.5 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142.5 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 146.6666 | 40 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160 | 40 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1304.3333 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1799.1416 | 52.25 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2161.4874 | 270.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 501.1767 | 16.45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.4 | 4.4 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | NPCC | Summer | 13120.9566 | 154.85 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3.8 | 4.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142.1 | 49 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 207 | 69 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1535.675 | 251.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2987.5 | 30 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4295.5 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3890 | 30 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7975 | 50 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1245.8333 | 25 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | NPCC | Winter | 16401.1958 | 147.25 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65.4167 | 25 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3878.1167 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3945.4 | 12 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3651.6667 | 20 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 413 | 7 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 419.4 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 481.0166 | 66.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 536.75 | 28.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28166.8 | 67 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1676.6667 | 20 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7659.1666 | 65 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 755 | 5 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25777.6664 | 340 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | LI | 100 | Fossil-Steam | NPCC | Off-Peak | 4111.2675 | 154.85 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.5167 | 17 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 324 | 27 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 810 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 965.25 | 429 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1951.4582 | 275.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37 | 37 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82 | 41 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1527.2832 | 251.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1674.8333 | 65 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 79.8 | 18 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 310.2999 | 87 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2480.85 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 6800.0533 | 35.2 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 633.65 | 23 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 291.3333 | 23 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 436.3667 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 301.4667 | 38 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1670 | 20 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 4147.7 | 38 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1426.4 | 48 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 342 | 38 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 7328 | 48 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 69.6 | 58 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1496.9167 | 23 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 635.25 | 33 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 418.1667 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1314 | 18 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 9600.7 | 38 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 521.7 | 18 | 1 | 1 | 1140-First superheater | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3885.6 | 18 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5947.9 | 293 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 91 | 28 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1862 | 38 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1105.8166 | 43 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 366.3333 | 28 | 1 | 1 | 1140-First superheater | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1586.2167 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 57.9 | 18 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1589.6667 | 38 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 527.3333 | 28 | 1 | 1 | 1140-First superheater | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1329.5998 | 288 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 885.5 | 23 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2792.5333 | 68 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2320.8 | 48 | 1 | 1 | 1140-First superheater | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 100 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 850.45 | 233 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 393.3 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 423.7 | 38 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2185.4 | 42 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7831.9999 | 240 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.6 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 504 | 252 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5610.6666 | 320 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 965.2767 | 28.7 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4436.9166 | 185 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21021 | 382.2 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1121.2666 | 278 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65402.95 | 577 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.3333 | 92 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2958 | 493 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 779 | 82 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 289.8 | 27 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 539.75 | 127 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9995.8332 | 125 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2316 | 386 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27533.3332 | 200 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2015 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7593.75 | 75 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.8333 | 10 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.75 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456.5 | 166 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131.25 | 21 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238 | 70 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357.9 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 934.1999 | 162 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1154 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68201.4 | 577 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 251.6666 | 100 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 387.1665 | 202 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.4 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 617.5 | 57 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1108.1 | 42 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 476.9165 | 295 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 179 | 179 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 995.8333 | 125 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 600 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1031.8 | 268 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1422 | 355.5 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2059 | 411.8 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 361.8332 | 167 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.5 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.9 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91 | 21 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 199.3333 | 23 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1658.9 | 313 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 233.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24121.3331 | 395 | 1 | 1 | 1150-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1373.75 | 157 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2 | 18 | 1 | 2 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187 | 34 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 932.2833 | 61 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92.25 | 27 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2257.3333 | 40 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 714 | 238 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2729.97 | 303.33 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1615.4999 | 270 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 243.75 | 117 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 288.3498 | 237 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.1 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.4 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 331.2 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 400.5 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 858 | 18 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1367.4667 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2326.3333 | 70 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1742.4 | 363 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1395.3332 | 280 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16323.3332 | 200 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 145.2 | 11 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 986.1 | 38 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 25.8333 | 31 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 32.2 | 46 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 104.8833 | 31 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 133.5 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 160.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 178.75 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 403.5166 | 31 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 551 | 29 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 570.75 | 45 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 128.2833 | 43 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 464 | 29 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 511.8 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 514.9166 | 37 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7.2 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 15 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 16.1 | 46 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 115.3166 | 37 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 159 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 226.8667 | 41 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 655.5 | 38 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 836.6333 | 38 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 29 | 29 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 57.85 | 13 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 188 | 48 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 11.5 | 46 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 17.6333 | 46 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 20.75 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 24.6666 | 37 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 84 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 119.35 | 33 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 271.25 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 306.95 | 21 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 709.45 | 21 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 18.3667 | 29 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 23 | 46 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 49.6 | 48 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1438.8 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3691.3333 | 40 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 446.9333 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6 | 40 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107.7666 | 61 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 145.8333 | 70 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1221 | 3 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7177.5 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 742.5 | 150 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 917 | 60 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1080.8333 | 25 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90 | 18 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 710.6667 | 20 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.75 | 35 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 901.7166 | 131 | 1 | 1 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 46438.3331 | 745 | 1 | 1 | 1160-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 822.1667 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.2 | 12 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 371.8333 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 709 | 60 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1699.2 | 192 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10194 | 40 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2188 | 20 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1185.7999 | 231 | 1 | 1 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 396 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.5 | 50 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86.8 | 62 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 413 | 30 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 542.5 | 62 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 662.5 | 50 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 731.25 | 45 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 766.3333 | 190 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.4167 | 5 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 531.5666 | 74 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2015 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.75 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam